Solutions Manual

for

Introduction to Thermodynamics and Heat Transfer

Yunus A. Cengel

2nd Edition, 2008

Chapter 16

# HEAT EXCHANGERS

# PROPRIETARY AND CONFIDENTIAL

This Manual is the proprietary property of The McGraw-Hill Companies, Inc. (“McGraw-Hill”) and protected by copyright and other state and federal laws.  By opening and using this Manual the user agrees to the following restrictions, and if the recipient does not agree to these restrictions, the Manual should be promptly returned unopened to McGraw-Hill:  This Manual is being provided only to authorized professors and instructors for use in preparing for the classes using the affiliated textbook.  No other use or distribution of this Manual is permitted.  This Manual may not be sold and may not be distributed to or used by any student or other third party.  No part of this Manual may be reproduced, displayed or distributed in any form or by any means, electronic or otherwise, without the prior written permission of McGraw-Hill.

Types of Heat Exchangers

16-1C Heat exchangers are classified according to the flow type as parallel flow, counter flow, and cross-flow arrangement. In parallel flow, both the hot and cold fluids enter the heat exchanger at the same end and move in the same direction. In counter-flow, the hot and cold fluids enter the heat exchanger at opposite ends and flow in opposite direction. In cross-flow, the hot and cold fluid streams move perpendicular to each other.

16-2C In terms of construction type, heat exchangers are classified as compact, shell and tube and regenerative heat exchangers. Compact heat exchangers are specifically designed to obtain large heat transfer surface areas per unit volume. The large surface area in compact heat exchangers is obtained by attaching closely spaced thin plate or corrugated fins to the walls separating the two fluids. Shell and tube heat exchangers contain a large number of tubes packed in a shell with their axes parallel to that of the shell. Regenerative heat exchangers involve the alternate passage of the hot and cold fluid streams through the same flow area. In compact heat exchangers, the two fluids usually move perpendicular to each other.

16-3C A heat exchanger is classified as being compact if  > 700 m2/m3 or (200 ft2/ft3) where  is the ratio of the heat transfer surface area to its volume which is called the area density.  The area density for double-pipe heat exchanger can not be in the order of 700. Therefore, it can not be classified as a compact heat exchanger.

16-4C In counter-flow heat exchangers, the hot and the cold fluids move parallel to each other but both enter the heat exchanger at opposite ends and flow in opposite direction. In cross-flow heat exchangers, the two fluids usually move perpendicular to each other. The cross-flow is said to be unmixed when the plate fins force the fluid to flow through a particular interfin spacing and prevent it from moving in the transverse direction. When the fluid is free to move in the transverse direction, the cross-flow is said to be mixed.

16-5C In the shell and tube exchangers, baffles are commonly placed in the shell to force the shell side fluid to flow across the shell to enhance heat transfer and to maintain uniform spacing between the tubes. Baffles disrupt the flow of fluid, and an increased pumping power will be needed to maintain flow. On the other hand, baffles eliminate dead spots and increase heat transfer rate.

16-6C Using six-tube passes in a shell and tube heat exchanger increases the heat transfer surface area, and the rate of heat transfer increases. But it also increases the manufacturing costs.

16-7C Using so many tubes increases the heat transfer surface area which in turn increases the rate of heat transfer.

16-8C Regenerative heat exchanger involves the alternate passage of the hot and cold fluid streams through the same flow area.  The static type regenerative heat exchanger is basically a porous mass which has a large heat storage capacity, such as a ceramic wire mash.  Hot and cold fluids flow through this porous mass alternately.  Heat is transferred from the hot fluid to the matrix of the regenerator during the flow of the hot fluid and from the matrix to the cold fluid.  Thus the matrix serves as a temporary heat storage medium.  The dynamic type regenerator involves a rotating drum and continuous flow of the hot and cold fluid through different portions of the drum so that any portion of the drum passes periodically through the hot stream, storing heat and then through the cold stream, rejecting this stored heat.  Again the drum serves as the medium to transport the heat from the hot to the cold fluid stream.

The Overall Heat Transfer Coefficient

16-9C Heat is first transferred from the hot fluid to the wall by convection, through the wall by conduction and from the wall to the cold fluid again by convection.

16-10C When the wall thickness of the tube is small and the thermal conductivity of the tube material is high, which is usually the case, the thermal resistance of the tube is negligible.

16-11C The heat transfer surface areas are Ai=πD1L  and  Ao=πD2L. When the thickness of inner tube is small, it is reasonable to assume Ai≃Ao≃As.

16-12C No, it is not reasonable to say  hi≈h0≈h

16-13C When the wall thickness of the tube is small and the thermal conductivity of the tube material is high, the thermal resistance of the tube is negligible and the inner and the outer surfaces of the tube are almost identical (Ai≃Ao≃As).  Then the overall heat transfer coefficient of a heat exchanger can be determined to from U = (1/hi + 1/ho)-1

16-14C None.

16-15C When one of the convection coefficients is much smaller than the other hi<<ho, and Ai≈A0≈As. Then we have (1hi>>1ho) and thus Ui=U0=U≃hi.

16-16C The most common type of fouling is the precipitation of solid deposits in a fluid on the heat transfer surfaces.  Another form of fouling is corrosion and other chemical fouling.  Heat exchangers may also be fouled by the growth of algae in warm fluids.  This type of fouling is called the biological fouling.  Fouling represents additional resistance to heat transfer and causes the rate of heat transfer in a heat exchanger to decrease, and the pressure drop to increase.

16-17C The effect of fouling on a heat transfer is represented by a fouling factor Rf. Its effect on the heat transfer coefficient is accounted for by introducing a thermal resistance Rf /As. The fouling increases with increasing temperature and decreasing velocity.

16-18 The heat transfer coefficients and the fouling factors on tube and shell side of a heat exchanger are given. The thermal resistance and the overall heat transfer coefficients based on the inner and outer areas are to be determined.

Assumptions 1 The heat transfer coefficients and the fouling factors are constant and uniform.

Analysis (a) The total thermal resistance of the heat exchanger per unit length is

Outer surface

D0, A0, h0, U0 , Rf0

Inner surface

Di,  Ai, hi, Ui , Rfi

R=1hiAi+RfiAi+ln(DoDi)2πkL+RfoAo+1hoAoR=1(700 W/m2.°C)[π(0.012 m)(1 m)]+(0.0005 m2.°C/W)[π(0.012 m)(1 m)]+ln(1.61.2)2π(380 W/m.°C)(1 m)+(0.0002 m2.°C/W)[π(0.016 m)(1 m)]+1(700 W/m2.°C)[π(0.016 m)(1 m)]   =0.0837°C/W

(b) The overall heat transfer coefficient based on the inner and the outer surface areas of the tube per length are

R=1UA=1UiAi=1UoAoUi=1RAi=1(0.0837°C/W)[π(0.012 m)(1 m)]=317 W/m2.°CUo=1RAo=1(0.0837°C/W)[π(0.016 m)(1 m)]=238 W/m2.°C

16-19 EES Prob. 16-18 is reconsidered. The effects of pipe conductivity and heat transfer coefficients on the thermal resistance of the heat exchanger are to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

k=380 [W/m-C]

D_i=0.012 [m]

D_o=0.016 [m]

D_2=0.03 [m]

h_i=700 [W/m^2-C]

h_o=1400 [W/m^2-C]

R_f_i=0.0005 [m^2-C/W]

R_f_o=0.0002 [m^2-C/W]

"ANALYSIS"

R=1/(h_i*A_i)+R_f_i/A_i+ln(D_o/D_i)/(2*pi*k*L)+R_f_o/A_o+1/(h_o*A_o)

L=1 [m] “a unit length of the heat exchanger is considered"

A_i=pi*D_i*L

A_o=pi*D_o*L

| k [W/m-C] | R [C/W] |
| --- | --- |
| 10 | 0.07392 |
| 30.53 | 0.07085 |
| 51.05 | 0.07024 |
| 71.58 | 0.06999 |
| 92.11 | 0.06984 |
| 112.6 | 0.06975 |
| 133.2 | 0.06969 |
| 153.7 | 0.06964 |
| 174.2 | 0.06961 |
| 194.7 | 0.06958 |
| 215.3 | 0.06956 |
| 235.8 | 0.06954 |
| 256.3 | 0.06952 |
| 276.8 | 0.06951 |
| 297.4 | 0.0695 |
| 317.9 | 0.06949 |
| 338.4 | 0.06948 |
| 358.9 | 0.06947 |
| 379.5 | 0.06947 |
| 400 | 0.06946 |

| hi [W/m2-C] | R [C/W] |
| --- | --- |
| 500 | 0.08462 |
| 550 | 0.0798 |
| 600 | 0.07578 |
| 650 | 0.07238 |
| 700 | 0.06947 |
| 750 | 0.06694 |
| 800 | 0.06473 |
| 850 | 0.06278 |
| 900 | 0.06105 |
| 950 | 0.05949 |
| 1000 | 0.0581 |
| 1050 | 0.05684 |
| 1100 | 0.05569 |
| 1150 | 0.05464 |
| 1200 | 0.05368 |
| 1250 | 0.05279 |
| 1300 | 0.05198 |
| 1350 | 0.05122 |
| 1400 | 0.05052 |
| 1450 | 0.04987 |
| 1500 | 0.04926 |

| ho [W/m2-C] | R [C/W] |
| --- | --- |
| 1000 | 0.07515 |
| 1050 | 0.0742 |
| 1100 | 0.07334 |
| 1150 | 0.07256 |
| 1200 | 0.07183 |
| 1250 | 0.07117 |
| 1300 | 0.07056 |
| 1350 | 0.06999 |
| 1400 | 0.06947 |
| 1450 | 0.06898 |
| 1500 | 0.06852 |
| 1550 | 0.06809 |
| 1600 | 0.06769 |
| 1650 | 0.06731 |
| 1700 | 0.06696 |
| 1750 | 0.06662 |
| 1800 | 0.06631 |
| 1850 | 0.06601 |
| 1900 | 0.06573 |
| 1950 | 0.06546 |
| 2000 | 0.0652 |

16-20 A water stream is heated by a jacketted-agitated vessel, fitted with a turbine agitator. The mass flow rate of water is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The properties of water at 54C are (Table A-15)

k=0.648 W/m.°Cρ=985.8 kg/m3μ=0.513×10-3 kg/m⋅sPr=3.31

The specific heat of water at the average temperature of (10+54)/2=32C is 4178 J/kg.C (Table A-15)

Analysis We first determine the heat transfer coefficient on the inner wall of the vessel

Water

10ºC

54ºC

54ºC

Steam

100ºC

Re=nDa2ρμ=(60/60 s-1)(0.2 m)2(985.8 kg/m3)0.513×10−3 kg/m⋅s=76,865

Nu=0.76Re23Pr13=0.76(76,865)23(3.31)13=2048

hj=kDtNu=0.648 W/m.°C0.6 m(2048)=2211 W/m2.°C

The heat transfer coefficient on the outer side is determined as follows

ho=13,100(Tg−Tw)−0.25=13,100(100−Tw)−0.25

ho(Tg−Tw)=hj(Tw−54)13,100(100−Tw)−0.25(100−Tw)=2211(Tw−54)13,100(100−Tw)0.75=2211(Tw−54)→Tw=89.2°C

ho=13,100(100−Tw)−0.25=13,100(100−89.2)−0.25=7226 W/m2⋅C

Neglecting the wall resistance and the thickness of the wall, the overall heat transfer coefficient can be written as

U=1hj+1ho−1=12211+17226−1=1694 W/m2⋅C

From an energy balance

[mc(Tout−Tin)]water=UAΔTmw(4178)(54−10)=(1694)(π×0.6×0.6)(100−54)mw=0.479 kg/s=1725 kg/h

16-21 Water flows through the tubes in a boiler. The overall heat transfer coefficient of this boiler based on the inner surface area is to be determined.

Assumptions 1 Water flow is fully developed. 2 Properties of the water are constant.

Properties The properties of water at 110C are (Table A-15)

Outer surface

D0, A0, h0, U0 , Rf0

Inner surface

Di,  Ai, hi, Ui , Rfi

ν=μρ=0.268×10−6 m2/sk=0.682 W/m2.KPr=1.58

Analysis The Reynolds number is

Re=VavgDhν=(3.5 m/s)(0.01 m)0.268×10−6 m2s=130,600

which is greater than 10,000.  Therefore, the flow is turbulent.  Assuming fully developed flow,

Nu=hDhk=0.023Re0.8Pr0.4=0.023(130,600)0.8(1.58)0.4=342

and	h=kDhNu=0.682 W/m.°C0.01 m(342)=23,324 W/m2.°C

The total resistance of this heat exchanger is then determined from

R=Rtotal=Ri+Rwall+Ro=1hiAi+ln(DoDi)2πkL+1hoAo  =1(23,324 W/m2.°C)[π(0.01 m)(5 m)]+ln(1.41)[2π(14.2 W/m.°C)(5 m)]   +1(8400 W/m2.°C)[π(0.014 m)(5 m)]0.00157°C/W

and

R=1UiAiUi=1RAi=1(0.00157°C/W)[π(0.01 m)(5 m)]=4055 W/m2.°C

16-22 Water is flowing through the tubes in a boiler. The overall heat transfer coefficient of this boiler based on the inner surface area is to be determined.

Assumptions 1 Water flow is fully developed. 2 Properties of water are constant. 3 The heat transfer coefficient and the fouling factor are constant and uniform.

Outer surface

D0, A0, h0, U0 , Rf0

Inner surface

Di,  Ai, hi, Ui , Rfi

Properties The properties of water at 110C are (Table A-15)

ν=μρ=0.268×10−6 m2/sk=0.682 W/m2.KPr=1.58

Analysis The Reynolds number is

Re=VavgDhν=(3.5 m/s)(0.01 m)0.268×10−6 m2s=130,600

which is greater than 10,000. Therefore, the flow is turbulent.  Assuming fully developed flow,

Nu=hDhk=0.023Re0.8Pr0.4=0.023(130,600)0.8(1.58)0.4=342

and	h=kDhNu=0.682 W/m.°C0.01 m(342)=23,324 W/m2.°C

The thermal resistance of heat exchanger with a fouling factor of Rf,i=0.0005 m2.°C/W is determined from

R=1hiAi+Rf,iAi+ln(DoDi)2πkL+1hoAoR=1(23,324 W/m2.°C)[π(0.01 m)(5 m)]+0.0005 m2.°C/W[π(0.01 m)(5 m)]+ln(1.41)2π(14.2 W/m.°C)(5 m)+1(8400 W/m2.°C)[π(0.014 m)(5 m)]   =0.00475°C/W

Then,

R=1UiAiUi=1RAi=1(0.00475°C/W)[π(0.01 m)(5 m)]=1340 W/m2.°C

16-23 EES Prob. 16-22 is reconsidered. The overall heat transfer coefficient based on the inner surface as a function of fouling factor is to be plotted.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_w=110 [C]

Vel=3.5 [m/s]

L=5 [m]

k_pipe=14.2 [W/m-C]

D_i=0.010 [m]

D_o=0.014 [m]

h_o=8400 [W/m^2-C]

R_f_i=0.0005 [m^2-C/W]

"PROPERTIES"

k=conductivity(Water, T=T_w, P=300)

Pr=Prandtl(Water, T=T_w, P=300)

rho=density(Water, T=T_w, P=300)

mu=viscosity(Water, T=T_w, P=300)

nu=mu/rho

"ANALYSIS"

Re=(Vel*D_i)/nu  "Re is calculated to be greater than 10,000. Therefore, the flow is turbulent."

Nusselt=0.023*Re^0.8*Pr^0.4

h_i=k/D_i*Nusselt

A_i=pi*D_i*L

A_o=pi*D_o*L

R=1/(h_i*A_i)+R_f_i/A_i+ln(D_o/D_i)/(2*pi*k_pipe*L)+1/(h_o*A_o)

U_i=1/(R*A_i)

| Rf,i [m2-C/W] | Ui [W/m2-C] |
| --- | --- |
| 0.0001 | 2883 |
| 0.00015 | 2520 |
| 0.0002 | 2238 |
| 0.00025 | 2013 |
| 0.0003 | 1829 |
| 0.00035 | 1675 |
| 0.0004 | 1546 |
| 0.00045 | 1435 |
| 0.0005 | 1339 |
| 0.00055 | 1255 |
| 0.0006 | 1181 |
| 0.00065 | 1115 |
| 0.0007 | 1056 |
| 0.00075 | 1003 |
| 0.0008 | 955.2 |

16-24 Refrigerant-134a is cooled by water in a double-pipe heat exchanger. The overall heat transfer coefficient is to be determined.

Assumptions 1 The thermal resistance of the inner tube is negligible since the tube material is highly conductive and its thickness is negligible. 2 Both the water and refrigerant-134a flow are fully developed. 3 Properties of the water and refrigerant-134a are constant.

Cold water

Hot R-134a

D0

Di

Properties The properties of water at 20C are (Table A-15)

ρ=998 kg/m3ν=μρ=1.004×10−6 m2/sk=0.598 W/m.°CPr=7.01

Analysis The hydraulic diameter for annular space is

Dh=Do−Di=0.025−0.01=0.015 m

The average velocity of water in the tube and the Reynolds  number are

Vavg=mρAc=mρπDo2−Di24=0.3 kg/s(998 kg/m3)π(0.025 m)2−(0.01 m)24=0.729 m/s

Re=VavgDhν=(0.729 m/s)(0.015 m)1.004×10−6 m2s=10,890

which is greater than 4000.  Therefore flow is turbulent.  Assuming fully developed flow,

Nu=hDhk=0.023Re0.8Pr0.4=0.023(10,890)0.8(7.01)0.4=85.0

and

ho=kDhNu=0.598 W/m.°C0.015 m(85.0)=3390 W/m2.°C

Then the overall heat transfer coefficient becomes

U=11hi+1ho=115000 W/m2.°C+13390 W/m2.°C=2020 W/m2.°C

16-25 Refrigerant-134a is cooled by water in a double-pipe heat exchanger. The overall heat transfer coefficient is to be determined.

Cold water

Hot R-134a

Limestone

D0

Di

Assumptions 1 The thermal resistance of the inner tube is negligible since the tube material is highly conductive and its thickness is negligible. 2 Both the water and refrigerant-134a flows are fully developed. 3 Properties of the water and refrigerant-134a are constant. 4 The limestone layer can be treated as a plain layer since its thickness is very small relative to its diameter.

Properties The properties of water at 20C are (Table A-15)

ρ=998 kg/m3ν=μρ=1.004×10−6 m2/sk=0.598 W/m.°CPr=7.01

Analysis The hydraulic diameter for annular space is

Dh=Do−Di=0.025−0.01=0.015 m

The average velocity of water in the tube and the Reynolds number are

Vavg=mρAc=mρπDo2−Di24=0.3 kg/s(998 kg/m3)π(0.025 m)2−(0.01 m)24=0.729 m/s

Re=VavgDhν=(0.729 m/s)(0.015 m)1.004×10−6 m2s=10,890

which is greater than 10,000.  Therefore flow is turbulent.  Assuming fully developed flow,

Nu=hDhk=0.023Re0.8Pr0.4=0.023(10,890)0.8(7.01)0.4=85.0

and

ho=kDhNu=0.598 W/m.°C0.015 m(85.0)=3390 W/m2.°C

Disregarding the curvature effects, the overall heat transfer coefficient is determined to be

U=11hi+Lklimeston+1ho=115000 W/m2.°C+0.002 m1.3 W/m.°C+13390 W/m2.°C=493 W/m2.°C

16-26 EES Prob. 16-25 is reconsidered. The overall heat transfer coefficient as a function of the limestone thickness is to be plotted.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

D_i=0.010 [m]

D_o=0.025 [m]

T_w=20 [C]

h_i=5000 [W/m^2-C]

m_dot=0.3 [kg/s]

L_limestone=2 [mm]

k_limestone=1.3 [W/m-C]

"PROPERTIES"

k=conductivity(Water, T=T_w, P=100)

Pr=Prandtl(Water, T=T_w, P=100)

rho=density(Water, T=T_w, P=100)

mu=viscosity(Water, T=T_w, P=100)

nu=mu/rho

"ANALYSIS"

D_h=D_o-D_i

Vel=m_dot/(rho*A_c)

A_c=pi*(D_o^2-D_i^2)/4

Re=(Vel*D_h)/nu

"Re is calculated to be greater than 10,000. Therefore, the flow is turbulent."

Nusselt=0.023*Re^0.8*Pr^0.4

h_o=k/D_h*Nusselt

U=1/(1/h_i+(L_limestone*Convert(mm, m))/k_limestone+1/h_o)

| Llimestone [mm] | U [W/m2-C] |
| --- | --- |
| 1 | 791.4 |
| 1.1 | 746 |
| 1.2 | 705.5 |
| 1.3 | 669.2 |
| 1.4 | 636.4 |
| 1.5 | 606.7 |
| 1.6 | 579.7 |
| 1.7 | 554.9 |
| 1.8 | 532.2 |
| 1.9 | 511.3 |
| 2 | 491.9 |
| 2.1 | 474 |
| 2.2 | 457.3 |
| 2.3 | 441.8 |
| 2.4 | 427.3 |
| 2.5 | 413.7 |
| 2.6 | 400.9 |
| 2.7 | 388.9 |
| 2.8 | 377.6 |
| 2.9 | 367 |
| 3 | 356.9 |

16-27E Water is cooled by air in a cross-flow heat exchanger. The overall heat transfer coefficient is to be determined.

Assumptions 1 The thermal resistance of the inner tube is negligible since the tube material is highly conductive and its thickness is negligible. 2 Both the water and air flow are fully developed. 3 Properties of the water and air are constant.

Properties The properties of water at 180F are (Table A-15E)

Water

180F

4 ft/s

Air

80F

12 ft/s

k=0.388 Btu/h.ft.°Fν=3.825×10−6 ft2sPr=2.15

The properties of air at 80F are (Table A-22E)

k=0.01481 Btu/h.ft.°Fν=1.697×10−4 ft2sPr=0.7290

Analysis The overall heat transfer coefficient can be determined from

1U=1hi+1ho

The Reynolds number of water is

Re=VavgDhν=(4 ft/s)[0.75/12 ft]3.825×10−6 ft2s=65,360

which is greater than 10,000. Therefore the flow of water is turbulent. Assuming the flow to be fully developed, the Nusselt number is determined from

Nu=hDhk=0.023Re0.8Pr0.4=0.023(65,360)0.8(2.15)0.4=222

and	hi=kDhNu=0.388 Btu/h.ft.°F0.7512 ft(222)=1378 Btu/h.ft2.°F

The Reynolds number of air is

Re=VDν=(12 ft/s)[3/(4×12) ft]1.697×10−4 ft2s=4420

The flow of air is across the cylinder. The proper relation for Nusselt number in this case is

Nu=hDk=0.3+0.62Re0.5Pr131+0.4/Pr23141+Re282,0005845               =0.3+0.62(4420)0.5(0.7290)131+0.40.729023141+4420282,0005845=34.86

and	ho=kDNu=0.01481 Btu/h.ft.°F0.7512 ft(34.86)=8.26 Btu/h.ft2.°F

Then the overall heat transfer coefficient becomes

U=11hi+1ho=111378 Btu/h.ft2.°F+18.26 Btu/h.ft2.°F=8.21 Btu/h.ft2.°F

Analysis of Heat Exchangers

16-28C The heat exchangers usually operate for long periods of time with no change in their operating conditions, and then they can be modeled as steady-flow devices. As such , the mass flow rate of each fluid remains constant and the fluid properties such as temperature and velocity at any inlet and outlet remain constant. The kinetic and potential energy changes are negligible. The specific heat of a fluid can be treated as constant in a specified temperature range. Axial heat conduction along the tube is negligible.  Finally, the outer surface of the heat exchanger is assumed to be perfectly insulated so that there is no heat loss to the surrounding medium and any heat transfer thus occurs is between the two fluids only.

16-29C That relation is valid under steady operating conditions, constant specific heats, and negligible heat loss from the heat exchanger.

16-30C The product of the mass flow rate and the specific heat of a fluid is called the heat capacity rate and is expressed as C=mcp. When the heat capacity rates of the cold and hot fluids are equal, the temperature change is the same for the two fluids in a heat exchanger. That is, the temperature rise of the cold fluid is equal to the temperature drop of the hot fluid.  A heat capacity of infinity for a fluid in a heat exchanger is experienced during a phase-change process in a condenser or boiler.

16-31C The mass flow rate of the cooling water can be determined from Q=(mcpΔT)cooling water. The rate of condensation of the steam is determined from Q=(mhfg)steam, and the total thermal resistance of the condenser is determined from R=QΔT.

16-32C When the heat capacity rates of the cold and hot fluids are identical, the temperature rise of the cold fluid will be equal to the temperature drop of the hot fluid.

The Log Mean Temperature Difference Method

16-33C Tlm is called the log mean temperature difference, and is expressed as

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)

where

ΔT1=Th,in−Tc,in       ΔT2=Th,out−Tc,out	for parallel-flow heat exchangers and

ΔT=Th,in−Tc,out      ΔT2=Th,out−Tc,in	for counter-flow heat exchangers

16-34C The temperature difference between the two fluids decreases from T1 at the inlet to T2 at the outlet, and arithmetic mean temperature difference is defined as ΔTam=ΔT1+ΔT22. The logarithmic mean temperature difference Tlm is obtained by tracing the actual temperature profile of the fluids along the heat exchanger, and is an exact representation of the average temperature difference between the hot and cold fluids. It truly reflects the exponential decay of the local temperature difference. The logarithmic mean temperature difference is always less than the arithmetic mean temperature.

16-35C Tlm cannot be greater than both T1 and T2 because Tln is always less than or equal to Tm (arithmetic mean) which can not be greater than both T1 and  T2.

16-36C No, it cannot. When T1 is less than T2 the ratio of them must be less than one and  the natural logarithms of the numbers which are less than 1 are negative. But the numerator is also negative in this case. When T1 is greater than T2, we obtain positive numbers at the both numerator and denominator.

16-37C In the parallel-flow heat exchangers the hot and cold fluids enter the heat exchanger at the same end, and the temperature of the hot fluid decreases and the temperature of the cold fluid increases along the heat exchanger. But the temperature of the cold fluid can never exceed that of the hot fluid.  In case of the counter-flow heat exchangers the hot and cold fluids enter the heat exchanger from the opposite ends and the outlet temperature of the cold fluid may exceed the outlet temperature of the hot fluid.

16-38C The Tlm will be greatest for double-pipe counter-flow heat exchangers.

16-39C The factor F is called as correction factor which depends on the geometry of the heat exchanger and the inlet and the outlet temperatures of the hot and cold fluid streams. It represents how closely a heat exchanger approximates a counter-flow heat exchanger in terms of its logarithmic mean temperature difference. F cannot be greater than unity.

16-40C In this case it is not practical to use the LMTD method because it requires tedious iterations. Instead, the effectiveness-NTU method should be used.

16-41C First heat transfer rate is determined from Q=mcp[Tin−Tout], Tln from ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2), correction factor from the figures, and finally the surface area of the heat exchanger from  Q=UAFDTlm,CF

16-42 Ethylene glycol is heated in a tube while steam condenses on the outside tube surface. The tube length is to be determined.

Assumptions 1 Steady flow conditions exist. 2 The inner surfaces of the tubes are smooth. 3 Heat transfer to the surroundings is negligible.

Properties The properties of ethylene glycol are given to be  = 1109 kg/m3, cp = 2428 J/kgK, k = 0.253 W/mK, µ = 0.01545 kg/ms, Pr = 148.5. The thermal conductivity of copper is given to be 386 W/mK.

Analysis The rate of heat transfer is

Ethylene glycol

1 kg/s

20ºC

L

Tg = 110ºC

Q=mcp(Te−Ti)=(1 kg/s)(2428 J/kg.°C)(40−20)°C=48,560 W

The fluid velocity is

V=mρAc=1 kg/s(1109 kg/m3)π(0.02 m)24=2.870 m/s

The Reynolds number is

Re=ρVDμ=(1109 kg/m3)(2.870 m/s)(0.02 m)0.01545 kg/m⋅s=4121

which is greater than 2300 and smaller than 10,000. Therefore, we have transitional flow. We assume fully developed flow and evaluate the Nusselt number from turbulent flow relation:

Nu=hDk=0.023Re0.8Pr0.4=0.023(4121)0.8(148.5)0.4=132.5

Heat transfer coefficient on the inner surface is

hi=kDNu=0.253 W/m.°C0.02 m(132.5)=1677 W/m2.°C

Assuming a wall temperature of 100C, the heat transfer coefficient on the outer surface is determined to be

ho=9200(Tg−Tw)−0.25=9200(110−100)−0.25=5174 W/m2.°C

Let us check if the assumption for the wall temperature holds:

hiAi(Tw−Tb,avg)=hoAo(Tg−Tw)hiπDiL(Tw−Tb,avg)=hoπDoL(Tg−Tw)1677×0.02(Tw−30)=5174×0.025(110−Tw)Tw=93.5°C

Now we assume a wall temperature of 90C:

ho=9200(Tg−Tw)−0.25=9200(110−90)−0.25=4350 W/m2.°C

Again checking,	1677×0.02(Tw−30)=4350×0.025(110−Tw)Tw=91.1°C

which is sufficiently close to the assumed value of 90C. Now that both heat transfer coefficients are available, we use thermal resistance concept to find overall heat transfer coefficient based on the outer surface area as follows:

Uo=1DohiDi+Doln(D2D1)2kcopper+1ho=10.025(1677)(0.02)+(0.025)ln(2.52)2(386)+14350=1018 W/m2⋅C

The rate of heat transfer can be expressed as

Q=UoAoΔTln

where the logarithmic mean temperature difference is

ΔTlm=(Tg−Te)−(Tg−Ti)lnTg−TeTg−Ti=(110−40)−(110−20)ln110−40110−20=79.58°C

Substituting, the tube length is determined to be

Q=UoAoΔTln48,560=(1018)π(0.025)L(79.58)L=7.63 m

16-43 Water is heated in a double-pipe, parallel-flow uninsulated heat exchanger by geothermal water. The rate of heat transfer to the cold water and the log mean temperature difference for this heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heat of hot water is given to be 4.25 kJ/kg.C.

Cold

water

Hot water

85C

50C

Analysis The rate of heat given up by the hot water is

Qh=[mcp(Tin−Tout)]hot water(1.4 kg/s)(4.25 kJ/kg.°C)(85°C−50°C)=208.3 kW

The rate of heat picked up by the cold water is

Qc=(1−0.03)Qh=(1−0.03)(208.3 kW)=202.0 kW

The log mean temperature difference is

Q=UAΔTlmΔTlm==QUA=202.0 kW(1.15 kW/m2⋅°C)(4 m2)=43.9°C

16-44 A stream of hydrocarbon is cooled by water in a double-pipe counterflow heat exchanger. The overall heat transfer coefficient is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of hydrocarbon and water are given to be 2.2 and 4.18 kJ/kg.C, respectively.

Analysis The rate of heat transfer is

Q=[mcp(Tout−Tin)]HC=(7203600 kg/s)(2.2 kJ/kg.°C)(150°C−40°C)=48.4 kW

The outlet temperature of water is

Water

10C

HC

150C

40C

Q=[mcp(Tout−Tin)]w48.4 kW=(5403600 kg/s)(4.18 kJ/kg.°C)(Tw,out−10°C)Tw,out=87.2 °C

The logarithmic mean temperature difference is

ΔT1=Th,in−Tc,out=150°C−87.2°C=62.8°CΔT2=Th,out−Tc,in=40°C−10°C=30°C

and	ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=62.8−30ln(62.830)=44.4°C

The overall heat transfer coefficient is determined from

Q=UAΔTlm48.4 kW=U(π×0.025×6.0)(44.4°C)U=2.31 kW/m2⋅K

16-45 Oil is heated by water in a 1-shell pass and 6-tube passes heat exchanger. The rate of heat transfer and the heat transfer surface area are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heat of oil is given to be 2.0 kJ/kg.C.

Analysis The rate of heat transfer in this heat exchanger is

Q=[mcp(Tout−Tin)]oil=(10 kg/s)(2.0 kJ/kg.°C)(46°C−25°C)=420 kW

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

Water

80C

Oil

25C

10 kg/s

46C

1 shell pass

6 tube passes

60C

ΔT1=Th,in−Tc,out=80°C−46°C=34°CΔT2=Th,out−Tc,in=60°C−25°C=35°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=34−35ln(3435)=34.5°C

P=t2−t1T1−t1=46−2580−25=0.38F=0.94

Then the heat transfer surface area on the tube side becomes

Q=UAsFΔTlm,CFAs=QUFΔTlm,CF=420 kW(1.0 kW/m2.°C)(0.94)(34.5°C)=13.0 m2

16-46 Steam is condensed by cooling water in the condenser of a power plant. The mass flow rate of the cooling water and the rate of condensation are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The heat of vaporization of water at 50C is given to be hfg = 2383 kJ/kg and specific heat of cold water at the average temperature of 22.5C is given to be cp = 4180 J/kg.C.

Analysis The temperature differences between the steam and the cooling water at the two ends of the condenser are

Steam

50C

18C

Water

50C

27C

ΔT1=Th,in−Tc,out=50°C−27°C=23°CΔT2=Th,out−Tc,in=50°C−18°C=32°C

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=23−32ln(2332)=27.3°C

Then the heat transfer rate in the condenser becomes

Q=UAsΔTlm=(2400 W/m2.°C)(42 m2)(27.3°C)=2752 kW

The mass flow rate of the cooling water and the rate of condensation of steam are determined from

Q=[mcp(Tout−Tin)]cooling watermcooling water=Qcp(Tout−Tin)=2752 kJ/s(4.18 kJ/kg.°C)(27°C−18°C)=73.1 kg/s

Q=(mhfg)steammsteam=Qhfg=2752 kJ/s2383 kJ/kg=1.15 kg/s

16-47 Water is heated in a double-pipe parallel-flow heat exchanger by geothermal water. The required length of tube is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of water and geothermal fluid are given to be 4.18 and 4.31 kJ/kg.C, respectively.

Analysis The rate of heat transfer in the heat exchanger is

Q=[mcp(Tout−Tin)]water=(0.2 kg/s)(4.18 kJ/kg.°C)(60°C−25°C)=29.26 kW

Then the outlet temperature of the geothermal water is determined from

Water

25C

Brine

140C

60C

Q=[mcp(Tin−Tout)]geot.waterTout=Tin−Qmcp=140°C−29.26 kW(0.3 kg/s)(4.31 kJ/kg.°C)=117.4°C
The logarithmic mean temperature difference is

ΔT1=Th,in−Tc,in=140°C−25°C=115°CΔT2=Th,out−Tc,out=117.4°C−60°C=57.4°C

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=115−57.4ln(11557.4)=82.9°C

The surface area of the heat exchanger is determined from

Q=UAsΔTlmAs=QUΔTlm=29.26 kW(0.55 kW/m2)(82.9°C)=0.642 m2

Then the length of the tube required becomes

As=πDLL=AsπD=0.642 m2π(0.008 m)=25.5 m

16-48 EES Prob. 16-47 is reconsidered. The effects of temperature and mass flow rate of geothermal water on the length of the tube are to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_w_in=25 [C]

T_w_out=60 [C]

m_dot_w=0.2 [kg/s]

c_p_w=4.18 [kJ/kg-C]

T_geo_in=140 [C]

m_dot_geo=0.3 [kg/s]

c_p_geo=4.31 [kJ/kg-C]

D=0.008 [m]

U=0.55 [kW/m^2-C]

"ANALYSIS"

Q_dot=m_dot_w*c_p_w*(T_w_out-T_w_in)

Q_dot=m_dot_geo*c_p_geo*(T_geo_in-T_geo_out)

DELTAT_1=T_geo_in-T_w_in

DELTAT_2=T_geo_out-T_w_out

DELTAT_lm=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

Q_dot=U*A*DELTAT_lm

A=pi*D*L

| Tgeo,in [C] | L [m] |
| --- | --- |
| 100 | 53.73 |
| 105 | 46.81 |
| 110 | 41.62 |
| 115 | 37.56 |
| 120 | 34.27 |
| 125 | 31.54 |
| 130 | 29.24 |
| 135 | 27.26 |
| 140 | 25.54 |
| 145 | 24.04 |
| 150 | 22.7 |
| 155 | 21.51 |
| 160 | 20.45 |
| 165 | 19.48 |
| 170 | 18.61 |
| 175 | 17.81 |
| 180 | 17.08 |
| 185 | 16.4 |
| 190 | 15.78 |
| 195 | 15.21 |
| 200 | 14.67 |

| mgeo [kg/s] | L [m] |
| --- | --- |
| 0.1 | 46.31 |
| 0.125 | 35.52 |
| 0.15 | 31.57 |
| 0.175 | 29.44 |
| 0.2 | 28.1 |
| 0.225 | 27.16 |
| 0.25 | 26.48 |
| 0.275 | 25.96 |
| 0.3 | 25.54 |
| 0.325 | 25.21 |
| 0.35 | 24.93 |
| 0.375 | 24.69 |
| 0.4 | 24.49 |
| 0.425 | 24.32 |
| 0.45 | 24.17 |
| 0.475 | 24.04 |
| 0.5 | 23.92 |

16-49E Glycerin is heated by hot water in a 1-shell pass and 8-tube passes heat exchanger. The rate of heat transfer for the cases of fouling and no fouling are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Heat transfer coefficients and fouling factors are constant and uniform. 5 The thermal resistance of the inner tube is negligible since the tube is thin-walled and highly conductive.

Properties The specific heats of glycerin and water are given to be 0.60 and 1.0 Btu/lbm.F, respectively.

Analysis (a) The tubes are thin walled and thus we assume the inner surface area of the tube to be equal to the outer surface area. Then the heat transfer surface area of this heat exchanger becomes

As=nπDL=8π(0.512 ft)(500 ft)=523.6 ft2

Glycerin

65F

175F

Hot Water

120F

140F

The temperature differences at the two ends of the heat exchanger are

ΔT1=Th,in−Tc,out=175°F−140°F=35°FΔT2=Th,out−Tc,in=120°F−65°F=55°F

and  ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=35−55ln(3555)=44.25°F

The correction factor is

P=t2−t1T1−t1=120−17565−175=0.5F=0.70

In case of no fouling, the overall heat transfer coefficient is determined from

U=11hi+1ho=1150 Btu/h.ft2.°F+14 Btu/h.ft2.°F=3.7 Btu/h.ft2.°F

Then the rate of heat transfer becomes

Q=UAsFΔTlm,CF=(3.7 Btu/h.ft2.°F)(523.6 ft2)(0.70)(44.25°F)=60,000 Btu/h

(b) The thermal resistance of the heat exchanger with a fouling factor is

R=1hiAi+RfiAi+1hoAo1(50 Btu/h.ft2.°F)(523.6 ft2)+0.002 h.ft2.°F/Btu523.6 ft2+1(4 Btu/h.ft2.°F)(523.6 ft2)   =0.0005195h.°F/Btu

The overall heat transfer coefficient in this case is

R=1UAsU=1RAs=1(0.0005195 h.°F/Btu)(523.6 ft2)=3.68 Btu/h.ft2.°F

Then rate of heat transfer becomes

Q=UAsFΔTlm,CF=(3.68 Btu/h.ft2.°F)(523.6 ft2)(0.70)(44.25°F)=59,680 Btu/h

16-50 During an experiment, the inlet and exit temperatures of water and oil and the mass flow rate of water are measured. The overall heat transfer coefficient based on the inner surface area is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The specific heats of water and oil are given to be 4180 and 2150 J/kg.C, respectively.

Analysis The rate of heat transfer from the oil to the water is

Q=[mcp(Tout−Tin)]water=(3 kg/s)(4.18 kJ/kg.°C)(55°C−20°C)=438.9 kW

The heat transfer area on the tube side is

Oil

120C

20C

Water

3 kg/s

55C

145C

24 tubes

Ai=nπDiL=24π(0.012 m)(2 m)=1.8 m2

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=120°C−55°C=65°CΔT2=Th,out−Tc,in=45°C−20°C=25°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=65−25ln(6525)=41.9°C

P=t2−t1T1−t1=55−20120−20=0.35F=0.70

Then the overall heat transfer coefficient becomes

Q=UiAiFΔTlm,CFUi=QAiFΔTlm,CF=438.9 kW(1.8 m2)(0.70)(41.9°C)=8.31 kW/m2.°C

16-51 Ethylene glycol is cooled by water in a double-pipe counter-flow heat exchanger. The rate of heat transfer, the mass flow rate of water, and the heat transfer surface area on the inner side of the tubes are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of water and ethylene glycol are given to be 4.18 and 2.56 kJ/kg.C, respectively.

Hot Glycol

80C

3.5 kg/s

Cold Water

20C

40C

55C

Analysis (a) The rate of heat transfer is

Q=[mcp(Tin−Tout)]glycol(3.5 kg/s)(2.56 kJ/kg.°C)(80°C−40°C)358.4 kW

(b) The rate of heat transfer from water must be equal to the rate of heat transfer to the glycol. Then,

Q=[mcp(Tout−Tin)]watermwater=Qcp(Tout−Tin)                                                             =358.4 kJ/s(4.18 kJ/kg.°C)(55°C−20°C)=2.45 kg/s

(c) The temperature differences at the two ends of the heat exchanger are

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=25−20ln(2520)=22.4°C

Then the heat transfer surface area becomes

Q=UiAiΔTlmAi=QUiΔTlm=358.4 kW(0.25 kW/m2.°C)(22.4°C)=64.0 m2

16-52 Water is heated by steam in a double-pipe counter-flow heat exchanger. The required length of the tubes is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heat of water is given to be 4.18 kJ/kg.C. The heat of condensation of steam at 120C is given to be 2203 kJ/kg.

Analysis The rate of heat transfer is

Water

17C

3 kg/s

Steam

120C

80C

Q=[mcp(Tout−Tin)]water(3 kg/s)(4.18 kJ/kg.°C)(80°C−17°C)=790.02 kW

The logarithmic mean temperature difference is

The heat transfer surface area is

Then the length of tube required becomes

Ai=πDiLL=AiπDi=7.9 m2π(0.025 m)=100.6 m

16-53 Oil is cooled by water in a thin-walled double-pipe counter-flow heat exchanger. The overall heat transfer coefficient of the heat exchanger is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant. 6 The thermal resistance of the inner tube is negligible since the tube is thin-walled and highly conductive.

Cold water

22C

1.5 kg/s

Hot oil

150C

2 kg/s

40C

Properties The specific heats of water and oil are given to be 4.18 and 2.20 kJ/kg.C, respectively.

Analysis The rate of heat transfer from the water to the oil is

Q=[mcp(Tin−Tout)]oil(2 kg/s)(2.2 kJ/kg.°C)(150°C−40°C)=484 kW

The outlet temperature of the water is determined from

Q=[mcp(Tout−Tin)]waterTout=Tin+Qmcp                                                          =22°C+484 kW(1.5 kg/s)(4.18 kJ/kg.°C)=99.2°C

The logarithmic mean temperature difference is

ΔT1=Th,in−Tc,out=150°C−99.2°C=50.8°CΔT2=Th,out−Tc,in=40°C−22°C=18°C

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=50.8−18ln(50.818)=31.6°C

Then the overall heat transfer coefficient becomes

U=QAsΔTlm=484 kWπ(0.025 m)(6 m)(31.6°C)=32.5 kW/m2.°C

16-54 EES Prob. 16-53 is reconsidered. The effects of oil exit temperature and water inlet temperature on the overall heat transfer coefficient of the heat exchanger are to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_oil_in=150 [C]

T_oil_out=40 [C]

m_dot_oil=2 [kg/s]

c_p_oil=2.20 [kJ/kg-C]

T_w_in=22 [C]

m_dot_w=1.5 [kg/s]

C_p_w=4.18 [kJ/kg-C]

D=0.025 [m]

L=6 [m]

"ANALYSIS"

Q_dot=m_dot_oil*c_p_oil*(T_oil_in-T_oil_out)

Q_dot=m_dot_w*c_p_w*(T_w_out-T_w_in)

DELTAT_1=T_oil_in-T_w_out

DELTAT_2=T_oil_out-T_w_in

DELTAT_lm=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

Q_dot=U*A*DELTAT_lm

A=pi*D*L

| Toil,out [C] | U [kW/m2-C] |
| --- | --- |
| 30 | 53.22 |
| 32.5 | 45.94 |
| 35 | 40.43 |
| 37.5 | 36.07 |
| 40 | 32.49 |
| 42.5 | 29.48 |
| 45 | 26.9 |
| 47.5 | 24.67 |
| 50 | 22.7 |
| 52.5 | 20.96 |
| 55 | 19.4 |
| 57.5 | 18 |
| 60 | 16.73 |
| 62.5 | 15.57 |
| 65 | 14.51 |
| 67.5 | 13.53 |
| 70 | 12.63 |

| Tw,in [C] | U [kW/m2C] |
| --- | --- |
| 5 | 20.7 |
| 6 | 21.15 |
| 7 | 21.61 |
| 8 | 22.09 |
| 9 | 22.6 |
| 10 | 23.13 |
| 11 | 23.69 |
| 12 | 24.28 |
| 13 | 24.9 |
| 14 | 25.55 |
| 15 | 26.24 |
| 16 | 26.97 |
| 17 | 27.75 |
| 18 | 28.58 |
| 19 | 29.46 |
| 20 | 30.4 |
| 21 | 31.4 |
| 22 | 32.49 |
| 23 | 33.65 |
| 24 | 34.92 |
| 25 | 36.29 |

16-55 The inlet and outlet temperatures of the cold and hot fluids in a double-pipe heat exchanger are given. It is to be determined whether this is a parallel-flow or counter-flow heat exchanger.

Analysis In parallel-flow heat exchangers, the temperature of the cold water can never exceed that of the hot fluid. In this case Tcold out = 50C which is greater than Thot out = 45C. Therefore this must be a counter-flow heat exchanger.

16-56 Cold water is heated by hot water in a double-pipe counter-flow heat exchanger. The rate of heat transfer and the heat transfer surface area of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant. 6 The thermal resistance of the inner tube is negligible since the tube is thin-walled and highly conductive.

Hot water

100C

3 kg/s

Cold Water

15C

1.25 kg/s

45C

Properties The specific heats of cold and hot water are given to be 4.18 and 4.19 kJ/kg.C, respectively.

Analysis The rate of heat transfer in this heat exchanger is

Q=[mcp(Tout−Tin)]cold water(1.25 kg/s)(4.18 kJ/kg.°C)(45°C−15°C)156.8 kW

The outlet temperature of the hot water is determined from

Q=[mcp(Tin−Tout)]hot waterTout=Tin−Qmcp=100°C−156.8 kW(3 kg/s)(4.19 kJ/kg.°C)=87.5°C

The temperature differences at the two ends of the heat exchanger are

ΔT1=Th,in−Tc,out=100°C−45°C=55°CΔT2=Th,out−Tc,in=87.5°C−15°C=72.5°C

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=55−72.5ln(5572.5)=63.3°C

Then the surface area of this heat exchanger becomes

Q=UAsΔTlmAs=QUΔTlm=156.8 kW(0.880 kW/m2.°C)(63.3°C)=2.81 m2

16-57 Engine oil is heated by condensing steam in a condenser. The rate of heat transfer and the length of the tube required are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant. 6 The thermal resistance of the inner tube is negligible since the tube is thin-walled and highly conductive.

Properties The specific heat of engine oil is given to be 2.1 kJ/kg.C. The heat of condensation of steam at 130C is given to be 2174 kJ/kg.

Analysis The rate of heat transfer in this heat exchanger is

Q=[mcp(Tout−Tin)]oil=(0.3 kg/s)(2.1 kJ/kg.°C)(60°C−20°C)=25.2 kW

Oil

20C

0.3 kg/s

Steam

130C

60C

The temperature differences at the two ends of the heat exchanger are

ΔT1=Th,in−Tc,out=130°C−60°C=70°CΔT2=Th,out−Tc,in=130°C−20°C=110°C

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=70−110ln(70110)=88.5°C

The surface area is

As=QUΔTlm=25.2 kW(0.65 kW/m2.°C)(88.5°C)=0.44 m2

Then the length of the tube required becomes

As=πDLL=AsπD=0.44 m2π(0.02 m)=7.0 m

16-58E Water is heated by geothermal water in a double-pipe counter-flow heat exchanger. The mass flow rate of each fluid and the total thermal resistance of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid.

Hot brine

270F

Cold Water

140F

180F

200F

3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of water and geothermal fluid are given to be 1.0 and 1.03 Btu/lbm.F, respectively.

Analysis The mass flow rate of each fluid is determined from

Q=[mcp(Tout−Tin)]watermwater=Qcp(Tout−Tin)=40 Btu/s(1.0 Btu/lbm.°F)(200°F−140°F)=0.667 lbm/s

Q=[mcp(Tout−Tin)]geo. watermgeo. water=Qcp(Tout−Tin)=40 Btu/s(1.03 Btu/lbm.°F)(270°F−180°F)=0.431 lbm/s

The temperature differences at the two ends of the heat exchanger are

ΔT1=Th,in−Tc,out=270°F−200°F=70°FΔT2=Th,out−Tc,in=180°F−140°F=40°F

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=70−40ln(7040)=53.61°F

Then

Q=UAsΔTlmUAs=QΔTlm=40 Btu/s53.61°F=0.7462 Btu/s.FU=1RAsR=1UAs=10.7462 Btu/s.°F=1.34 s⋅°F/Btu

16-59 Glycerin is heated by ethylene glycol in a thin-walled double-pipe parallel-flow heat exchanger. The rate of heat transfer, the outlet temperature of the glycerin, and the mass flow rate of the ethylene glycol are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant. 6 The thermal resistance of the inner tube is negligible since the tube is thin-walled and highly conductive.

Glycerin

20C

0.3 kg/s

Hot ethylene

60C

3 kg/s

Properties The specific heats of glycerin and ethylene glycol are given to be 2.4 and 2.5 kJ/kg.C, respectively.

Analysis (a) The temperature differences at the two ends are

ΔT1=Th,in−Tc,in=60°C−20°C=40°CΔT2=Th,out−Tc,out=Th,out−(Th,out−15°C)=15°C

and  	ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=40−15ln(4015)=25.5°C

Then the rate of heat transfer becomes

Q=UAsΔTlm=(240 W/m2.°C)(3.2 m2)(25.5°C)=19,584 W=19.58 kW

(b) The outlet temperature of the glycerin is determined from

Q=[mcp(Tout−Tin)]glycerinTout=Tin+Qmcp=20°C+19.584 kW(0.3 kg/s)(2.4 kJ/kg.°C)=47.2°C

(c) Then the mass flow rate of ethylene glycol becomes

Q=[mcp(Tin−Tout)]ethylene glycolmethylene glycol=Qcp(Tin−Tout)=19.584 kJ/s(2.5 kJ/kg.°C)[(47.2+15)°C−60°C]=3.56 kg/s

16-60 Air is preheated by hot exhaust gases in a cross-flow heat exchanger. The rate of heat transfer and the outlet temperature of the air are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Air

95 kPa

20C

0.8 m3/s

Exhaust gases

1.1 kg/s

95C

Properties The specific heats of air and combustion gases are given to be 1005 and 1100 J/kg.C, respectively.

Analysis The rate of heat transfer is

Q=[mcp(Tin−Tout)]gas.(1.1 kg/s)(1.1 kJ/kg.°C)(180°C−95°C)103 kW

The mass flow rate of air is

m=PVRT=(95 kPa)(0.8 m3/s)(0.287 kPa.m3/kg.K)×293 K=0.904 kg/s

Then the outlet temperature of the air becomes

Q=mcp(Tc,out−Tc,in)Tc,out=Tc,in+Qmcp=20°C+103×103 W(0.904 kg/s)(1005 J/kg.°C)=133°C

16-61 Water is heated by hot oil in a 2-shell passes and 12-tube passes heat exchanger. The heat transfer surface area on the tube side is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of water and oil are given to be 4.18 and 2.3 kJ/kg.C, respectively.

Analysis The rate of heat transfer in this heat exchanger is

Q=[mcp(Tout−Tin)]water=(4.5 kg/s)(4.18 kJ/kg.°C)(70°C−20°C)=940.5 kW

The outlet temperature of the oil is determined from

Q=[mcp(Tin−Tout)]oilTout=Tin−Qmcp=170°C−940.5 kW(10 kg/s)(2.3 kJ/kg.°C)=129°C

Oil

170C

10 kg/s

Water

20C

4.5 kg/s

70C

(12 tube passes)

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=170°C−70°C=100°CΔT2=Th,out−Tc,in=129°C−20°C=109°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=100−109ln(100109)=104.4°C

P=t2−t1T1−t1=70−20170−20=0.33F=1.0

Then the heat transfer surface area on the tube side becomes

Q=UAsFΔTlm,CFAs=QUFΔTlm,CF=940.5 kW(0.350 kW/m2.°C)(1.0)(104.4°C)=25.7 m2

16-62 Water is heated by hot oil in a 2-shell passes and 12-tube passes heat exchanger. The heat transfer surface area on the tube side is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of water and oil are given to be 4.18 and 2.3 kJ/kg.C, respectively.

Analysis The rate of heat transfer in this heat exchanger is

Q=[mcp(Tout−Tin)]water=(2 kg/s)(4.18 kJ/kg.°C)(70°C−20°C)=418 kW

The outlet temperature of the oil is determined from

Q=[mcp(Tin−Tout)]oilTout=Tin−Qmcp=170°C−418 kW(10 kg/s)(2.3 kJ/kg.°C)=151.8°C

Oil

170C

10 kg/s

Water

20C

2 kg/s

70C

(12 tube passes)

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=170°C−70°C=100°CΔT2=Th,out−Tc,in=151.8°C−20°C=131.8°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=100−131.8ln(100131.8)=115.2°C

P=t2−t1T1−t1=70−20170−20=0.33F=1.0

Then the heat transfer surface area on the tube side becomes

Q=UiAiFΔTlm,CFAi=QUiFΔTlm,CF=418 kW(0.350 kW/m2.°C)(1.0)(115.2°C)=10.4 m2

16-63 Ethyl alcohol is heated by water in a 2-shell passes and 8-tube passes heat exchanger. The heat transfer surface area of the heat exchanger is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of water and ethyl alcohol are given to be 4.19 and 2.67 kJ/kg.C, respectively.

Analysis The rate of heat transfer in this heat exchanger is

Q=[mcp(Tout−Tin)]ethyl alcohol=(2.1 kg/s)(2.67 kJ/kg.°C)(70°C−25°C)=252.3 kW

Water

95C

Ethyl

Alcohol

25C

2.1 kg/s

70C

(8 tube passes)

45C

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=95°C−70°C=25°CΔT2=Th,out−Tc,in=45°C−25°C=20°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=25−20ln(2520)=22.4°C

P=t2−t1T1−t1=70−2595−25=0.64F=0.82

Then the heat transfer surface area on the tube side becomes

Q=UiAiFΔTlm,CFAi=QUiFΔTlm,CF=252.3 kW(0.950 kW/m2.°C)(0.82)(22.4°C)=14.5 m2

16-64 Water is heated by ethylene glycol  in a 2-shell passes and 12-tube passes heat exchanger. The rate of heat transfer and the heat transfer surface area on the tube side are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of water and ethylene glycol are given to be 4.18 and 2.68 kJ/kg.C, respectively.

Analysis The rate of heat transfer in this heat exchanger is :

Q=[mcp(Tout−Tin)]water=(0.8 kg/s)(4.18 kJ/kg.°C)(70°C−22°C)=160.5 kW

Ethylene

110C

Water

22C

0.8 kg/s

70C

(12 tube passes)

60C

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=110°C−70°C=40°CΔT2=Th,out−Tc,in=60°C−22°C=38°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=40−38ln(4038)=39°C

P=t2−t1T1−t1=70−22110−22=0.55F=0.92

Then the heat transfer surface area on the tube side becomes

Q=UiAiFΔTlm,CFAi=QUiFΔTlm,CF=160.5 kW(0.28 kW/m2.°C)(0.92)(39°C)=16.0 m2

16-65 EES Prob. 16-64 is reconsidered. The effect of the mass flow rate of water on the rate of heat transfer and the tube-side surface area is to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_w_in=22 [C]

T_w_out=70 [C]

m_dot_w=0.8 [kg/s]

c_p_w=4.18 [kJ/kg-C]

T_glycol_in=110 [C]

T_glycol_out=60 [C]

c_p_glycol=2.68 [kJ/kg-C]

U=0.28 [kW/m^2-C]

"ANALYSIS"

Q_dot=m_dot_w*c_p_w*(T_w_out-T_w_in)

Q_dot=m_dot_glycol*c_p_glycol*(T_glycol_in-T_glycol_out)

DELTAT_1=T_glycol_in-T_w_out

DELTAT_2=T_glycol_out-T_w_in

DELTAT_lm_CF=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

P=(T_w_out-T_w_in)/(T_glycol_in-T_w_in)

R=(T_glycol_in-T_glycol_out)/(T_w_out-T_w_in)

F=0.92 "from Fig. 16-18b of the text at the calculated P and R"

Q_dot=U*A*F*DELTAT_lm_CF

| mw [kg/s] | Q [kW] | A [m2] |
| --- | --- | --- |
| 0.4 | 80.26 | 7.99 |
| 0.5 | 100.3 | 9.988 |
| 0.6 | 120.4 | 11.99 |
| 0.7 | 140.4 | 13.98 |
| 0.8 | 160.5 | 15.98 |
| 0.9 | 180.6 | 17.98 |
| 1 | 200.6 | 19.98 |
| 1.1 | 220.7 | 21.97 |
| 1.2 | 240.8 | 23.97 |
| 1.3 | 260.8 | 25.97 |
| 1.4 | 280.9 | 27.97 |
| 1.5 | 301 | 29.96 |
| 1.6 | 321 | 31.96 |
| 1.7 | 341.1 | 33.96 |
| 1.8 | 361.2 | 35.96 |
| 1.9 | 381.2 | 37.95 |
| 2 | 401.3 | 39.95 |
| 2.1 | 421.3 | 41.95 |
| 2.2 | 441.4 | 43.95 |

16-66E Steam is condensed by cooling water in a condenser. The rate of heat transfer, the rate of condensation of steam, and the mass flow rate of cold water are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant. 6 The thermal resistance of the inner tube is negligible since the tube is thin-walled and highly conductive.

Steam

90F

20 lbm/s

60F

Water

73F

90F

(8 tube passes)

Properties We take specific heat of water are given to be 1.0 Btu/lbm.F. The heat of condensation of steam at 90F is 1043 Btu/lbm.

Analysis (a) The log mean temperature difference is determined from

ΔT1=Th,in−Tc,out=90°F−73°F=17°FΔT2=Th,out−Tc,in=90°F−60°F=30°F

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=17−30ln(1730)=22.9°F

The heat transfer surface area is

As=8nπDL=8×50×π(348 ft)(5 ft)=392.7 ft2

and

Q=UAsΔTlm=(600 Btu/h.ft2.°F)(392.7 ft2)(22.9°F)=5.396×106 Btu/h

(b) The rate of condensation of the steam is

Q=(mhfg)steammsteam=Qhfg=5.396×106 Btu/h1043 Btu/lbm=5173 lbm/h=1.44 lbm/s

(c) Then the mass flow rate of cold water becomes

Q=[mcp(Tout−Tin)]cold watermcold water=Qcp(Tout−Tin)=5.396×106 Btu/h(1.0 Btu/lbm.°F)(73°F−60°F]=4.15×105 lbm/h=115 lbm/s

16-67E EES Prob. 16-66E is reconsidered. The effect of the condensing steam temperature on the rate of heat transfer, the rate of condensation of steam, and the mass flow rate of cold water is to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

N_pass=8

N_tube=50

T_steam=90 [F]

h_fg_steam=1043 [Btu/lbm]

T_w_in=60 [F]

T_w_out=73 [F]

c_p_w=1.0 [Btu/lbm-F]

D=3/4*1/12 [ft]

L=5 [ft]

U=600 [Btu/h-ft^2-F]

"ANALYSIS"

"(a)"

DELTAT_1=T_steam-T_w_out

DELTAT_2=T_steam-T_w_in

DELTAT_lm=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

A=N_pass*N_tube*pi*D*L

Q_dot=U*A*DELTAT_lm*Convert(Btu/h, Btu/s)

"(b)"

Q_dot=m_dot_steam*h_fg_steam

"(c)"

Q_dot=m_dot_w*c_p_w*(T_w_out-T_w_in)

| Tsteam [F] | Q [Btu/s] | msteam[lbm/s] | mw [lbm/s] |
| --- | --- | --- | --- |
| 80 | 810.5 | 0.7771 | 62.34 |
| 82 | 951.9 | 0.9127 | 73.23 |
| 84 | 1091 | 1.046 | 83.89 |
| 86 | 1228 | 1.177 | 94.42 |
| 88 | 1363 | 1.307 | 104.9 |
| 90 | 1498 | 1.436 | 115.2 |
| 92 | 1632 | 1.565 | 125.6 |
| 94 | 1766 | 1.693 | 135.8 |
| 96 | 1899 | 1.821 | 146.1 |
| 98 | 2032 | 1.948 | 156.3 |
| 100 | 2165 | 2.076 | 166.5 |
| 102 | 2297 | 2.203 | 176.7 |
| 104 | 2430 | 2.329 | 186.9 |
| 106 | 2562 | 2.456 | 197.1 |
| 108 | 2694 | 2.583 | 207.2 |
| 110 | 2826 | 2.709 | 217.4 |
| 112 | 2958 | 2.836 | 227.5 |
| 114 | 3089 | 2.962 | 237.6 |
| 116 | 3221 | 3.088 | 247.8 |
| 118 | 3353 | 3.214 | 257.9 |
| 120 | 3484 | 3.341 | 268 |

16-68 Glycerin is heated by hot water in a 1-shell pass and 20-tube passes heat exchanger. The mass flow rate of glycerin and the overall heat transfer coefficient of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heat of glycerin is given to be are given to be 2.48 kJ/kg.C and that of water is taken to be 4.18 kJ/kg.C.

Analysis The rate of heat transfer in this heat exchanger is

Q=[mcp(Tin−Tout)]water=(0.5 kg/s)(4.18 kJ/kg.°C)(100°C−55°C)=94.05 kW

The mass flow rate of the glycerin is determined from

Q=[mcp(Tout−Tin)]glycerinmglycerin=Qcp(Tout−Tin)=94.05 kJ/s(2.48 kJ/kg.°C)[(55°C−15°C]=0.95 kg/s

Glycerin

15C

100C

Hot Water

0.5 kg/s

55C

55C

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=100°C−55°C=45°CΔT2=Th,out−Tc,in=55°C−15°C=40°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=45−40ln(4540)=42.5°C

P=t2−t1T1−t1=55−10015−100=0.53F=0.77

The heat transfer surface area is

As=nπDL=20π(0.04 m)(2 m)=5.027 m2

Then the overall heat transfer coefficient of the heat exchanger is determined to be

Q=UAsFΔTlm,CFU=QAsFΔTlm,CF=94.05 kW(5.027 m2)(0.77)(42.5°C)=0.572 kW/m2.°C

16-69 Isobutane is condensed by cooling air in the condenser of a power plant. The mass flow rate of air and the overall heat transfer coefficient are to be determined.

Isobutane

75C

2.7 kg/s

Air, 21C

Air, 28C

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The heat of vaporization of isobutane at 75C is given to be hfg = 255.7 kJ/kg and specific heat of air is taken to be cp = 1005 J/kg.C.

Analysis First, the rate of heat transfer is determined from

Q=(mhfg)isobutane(2.7 kg/s)(255.7 kJ/kg)=690.4 kW

The mass flow rate of air is determined from

Q=[mcp(Tout−Tin)]airmair=Qcp(Tout−Tin)=690.4 kJ/s(1.005 kJ/kg.°C)(28°C−21°C)=98.1 kg/s

The temperature differences between the isobutane and the air at the two ends of the condenser are

ΔT1=Th,in−Tc,out=75°C−21°C=54°CΔT2=Th,out−Tc,in=75°C−28°C=47°C

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=54−47ln(5447)=50.4°C

Then the overall heat transfer coefficient is determined from

Q=UAsΔTlm690,400 W=U(24 m2)(50.4°C)U=571 W/m2.°C

16-70 Water is evaporated by hot exhaust gases in an evaporator. The rate of heat transfer, the exit temperature of the exhaust gases, and the rate of evaporation of water are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Water

200C

550C

Exhaust gases

Th,out

200C

Properties The heat of vaporization of water at 200C is given to be hfg = 1941 kJ/kg and specific heat of exhaust gases is given to be cp = 1051 J/kg.C.

Analysis The temperature differences between the water and the exhaust gases at the two ends of the evaporator are

ΔT1=Th,in−Tc,out=550°C−200°C=350°CΔT2=Th,out−Tc,in=(Th,out−200)°C

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=350−(Th,out−200)ln350(Th,out−200)

Then the rate of heat transfer can be expressed as

Q=UAsΔTlm=(1.780 kW/m2.°C)(0.5 m2)350−(Th,out−200)ln350(Th,out−200)   		(Eq. 1)

The rate of heat transfer can also be expressed as in the following forms

Q=[mcp(Th,in−Th,out)]exhaustgases=(0.25 kg/s)(1.051 kJ/kg.°C)(550°C−Th,out)	(Eq. 2)

Q=(mhfg)water=mwater(1941 kJ/kg)					(Eq. 3)

We have three equations with three unknowns. Using an equation solver such as EES, the unknowns are determined to be

Q=88.85 kWTh,out=211.8°Cmwater=0.0458 kg/s

16-71 EES Prob. 16-70 is reconsidered. The effect of the exhaust gas inlet temperature on the rate of heat transfer, the exit temperature of exhaust gases, and the rate of evaporation of water is to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_exhaust_in=550 [C]

c_p_exhaust=1.051 [kJ/kg-C]

m_dot_exhaust=0.25 [kg/s]

T_w=200 [C]

h_fg_w=1941 [kJ/kg]

A=0.5 [m^2]

U=1.780 [kW/m^2-C]

"ANALYSIS"

DELTAT_1=T_exhaust_in-T_w

DELTAT_2=T_exhaust_out-T_w

DELTAT_lm=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

Q_dot=U*A*DELTAT_lm

Q_dot=m_dot_exhaust*c_p_exhaust*(T_exhaust_in-T_exhaust_out)

Q_dot=m_dot_w*h_fg_w

| Texhaust,in [C] | Q [kW] | Texhaust,out [C] | mw [kg/s] |
| --- | --- | --- | --- |
| 300 | 25.39 | 203.4 | 0.01308 |
| 320 | 30.46 | 204.1 | 0.0157 |
| 340 | 35.54 | 204.7 | 0.01831 |
| 360 | 40.62 | 205.4 | 0.02093 |
| 380 | 45.7 | 206.1 | 0.02354 |
| 400 | 50.77 | 206.8 | 0.02616 |
| 420 | 55.85 | 207.4 | 0.02877 |
| 440 | 60.93 | 208.1 | 0.03139 |
| 460 | 66.01 | 208.8 | 0.03401 |
| 480 | 71.08 | 209.5 | 0.03662 |
| 500 | 76.16 | 210.1 | 0.03924 |
| 520 | 81.24 | 210.8 | 0.04185 |
| 540 | 86.32 | 211.5 | 0.04447 |
| 560 | 91.39 | 212.2 | 0.04709 |
| 580 | 96.47 | 212.8 | 0.0497 |
| 600 | 101.5 | 213.5 | 0.05232 |

16-72 The waste dyeing water is to be used to preheat fresh water. The outlet temperatures of each fluid and the mass flow rate are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 There is no fouling. 5 Fluid properties are constant.

Properties The specific heats of waste dyeing water and the fresh water are given to be cp = 4295 J/kg.C and  cp = 4180 J/kg.C, respectively.

Fresh

water

15C

Dyeing water

75C

Tc,out

Th,out

Analysis The temperature differences between the dyeing water and the fresh water at the two ends of the heat exchanger are

ΔT1=Th,in−Tc,out=75−Tc,outΔT2=Th,out−Tc,in=Th,out−15

and

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=(75−Tc,out)−(Th,out−15)ln(75−Tc,out)(Th,out−15)

Then the rate of heat transfer can be expressed as

Q=UAsΔTlm35 kW=(0.625 kW/m2.°C)(1.65 m2)(75−Tc,out)−(Th,out−15)ln(75−Tc,out)(Th,out−15)		(Eq. 1)

The rate of heat transfer can also be expressed as

Q=[mcp(Th,in−Th,out)]dyeingwater35 kW=m(4.295 kJ/kg.°C)(75°C−Th,out)	(Eq. 2)

Q=[mcp(Th,in−Th,out)]water35 kW=m(4.18 kJ/kg.°C)(Tc,out−15°C)	(Eq. 3)

We have three equations with three unknowns. Using an equation solver such as EES, the unknowns are determined to be

Tc,out=41.4°CTh,out=49.3°Cm=0.317 kg/s

The Effectiveness-NTU Method

16-73C When the heat transfer surface area A of the heat exchanger is known, but the outlet temperatures are not, the effectiveness-NTU method is definitely preferred.

16-74C The effectiveness of a heat exchanger is defined as the ratio of the actual heat transfer rate to the maximum possible heat transfer rate and represents how closely the heat transfer in the heat exchanger approaches to maximum possible heat transfer.  Since the actual heat transfer rate can not be greater than maximum possible heat transfer rate, the effectiveness can not be greater than one. The effectiveness of a heat exchanger depends on the geometry of the heat exchanger as well as the flow arrangement.

16-75C For a specified fluid pair, inlet temperatures and mass flow rates, the counter-flow heat exchanger will have the highest effectiveness.

16-76C Once the effectiveness εis known, the rate of heat transfer and the outlet temperatures of cold and hot fluids in a heat exchanger are determined from

Q=εQmax=εCmin(Th,in−Tc,in)Q=mccp,c(Tc,out−Tc,in)Q=mhcp,h(Th,in−Th,out)

16-77C The heat transfer in a heat exchanger will reach its maximum value when the hot fluid is cooled to the inlet temperature of the cold fluid. Therefore, the temperature of the hot fluid cannot drop below the inlet temperature of the cold fluid at any location in a heat exchanger.

16-78C The heat transfer in a heat exchanger will reach its maximum value when the cold fluid is heated to the inlet temperature of the hot fluid. Therefore, the temperature of the cold fluid cannot rise above the inlet temperature of the hot fluid at any location in a heat exchanger.

16-79C The fluid with the lower mass flow rate will experience a larger temperature change. This is clear from the relation

Q=mccpΔTcold=mhcpΔThot

16-80C The maximum possible heat transfer rate is in a heat exchanger is determined from

Qmax=Cmin(Th,in−Tc,in)

where Cmin is the smaller heat capacity rate. The value of Qmax does not depend on the type of heat exchanger.

16-81C The longer heat exchanger is more likely to have a higher effectiveness.

16-82C The increase of effectiveness with NTU is not linear. The effectiveness increases rapidly with NTU for small values (up to abo ut NTU = 1.5), but rather slowly for larger values. Therefore, the effectiveness will not double when the length of heat exchanger is doubled.

16-83C A heat exchanger has the smallest effectiveness value when the heat capacity rates of two fluids are identical. Therefore, reducing the mass flow rate of cold fluid by half will increase its effectiveness.

16-84C When the capacity ratio is equal to zero and the number of transfer units value is greater than 5, a counter-flow heat exchanger has an effectiveness of one. In this case the exit temperature of the fluid with smaller capacity rate will equal to inlet temperature of the other fluid. For a parallel-flow heat exchanger the answer would be the same.

16-85C The NTU of a heat exchanger is defined as NTU=UAsCmin=UAs(mcp)min where U is the overall heat transfer coefficient and As is the heat transfer surface area of the heat exchanger.  For specified values of U and Cmin, the value of NTU is a measure of the heat exchanger surface area As. Because the effectiveness increases slowly for larger values of NTU, a large heat exchanger cannot be justified economically. Therefore, a heat exchanger with a very large NTU is not necessarily a good one to buy.

16-86C The value of effectiveness increases slowly with a large values of NTU (usually larger than 3). Therefore, doubling the size of the heat exchanger will not save much energy in this case since the increase in the effectiveness will be very small.

16-87C The value of effectiveness increases rapidly with small values of NTU (up to about 1.5). Therefore, tripling the NTU will cause a rapid increase in the effectiveness of the heat exchanger, and thus saves energy. I would support this proposal.

16-88 Hot water coming from the engine of an automobile is cooled by air in the radiator. The outlet temperature of  the air and the rate of heat transfer are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The specific heats of water and air are given to be 4.00 and 1.00 kJ/kg.C, respectively.

Air

30C

10 kg/s

Coolant

80C

5 kg/s

Analysis (a) The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(5 kg/s)(4.00 kJ/kg.°C)=20 kW/°CCc=mccpc=(10 kg/s)(1.00 kJ/kg.°C)=10 kW/°C

Therefore   Cmin=Cc=10 kW/°C

which is the smaller of the two heat capacity rates. Noting that the heat capacity rate of the air is the smaller one, the outlet temperature of the air is determined from the effectiveness relation to be

ε=QQmax=Cmin(Ta,out−Tc,in)Cmin(Th,in−Tc,in)0.4=(Ta,out−30)°C(80−30)°CTa,out=50°C(b) The rate of heat transfer is determined from

Q=Cair(Ta,out−Ta,in)=(10 kW/°C)(50°C-30°C)=200 kW

16-89 The inlet and exit temperatures and the volume flow rates of hot and cold fluids in a heat exchanger are given. The rate of heat transfer to the cold water, the overall heat transfer coefficient, the fraction of heat loss, the heat transfer efficiency, the effectiveness, and the NTU of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Changes in the kinetic and potential energies of fluid streams are negligible. 3 Fluid properties are constant.

Properties The densities of hot water and cold water at the average temperatures of (71.5+58.2)/2 = 64.9C and (19.7+27.8)/2 = 23.8C are 980.5 and 997.3 kg/m3, respectively. The specific heat at the average temperature is 4187 J/kg.C for hot water and 4180 J/kg.C for cold water (Table A-15).

Analysis (a) The mass flow rates are

mh=ρhVh=(980.5 kg/m3)(0.00105/60 m3/s)=0.0172 kg/s

mc=ρcVc=(997.3 kg/m3)(0.00155/60 m3/s)=0.0258 kg/s

The rates of heat transfer from the hot water and to the cold water are

Qh=[mcp(Tin−Tout)]h=(0.0172 kg/s)(4187 kJ/kg.°C)(71.5°C−58.2°C)=957.8 W

Qc=[mcp(Tout−Tin)]c=(0.0258 kg/s)(4180 kJ/kg.°C)(27.8°C−19.2°C)=873.5 W

Hot

water

71.5C

Cold water

19.7C

27.8C

58.2C

(b) The number of shell and tubes are not specified in the problem. Therefore, we take the correction factor to be unity in the following calculations. The logarithmic mean temperature difference and the overall heat transfer coefficient are

ΔT1=Th,in−Tc,out=71.5°C−27.8°C=43.7°C

ΔT2=Th,out−Tc,in=58.2°C−19.7°C=38.5°C

ΔTlm=ΔT1−ΔT2lnΔT1ΔT2=43.7−38.5ln43.738.5=41.0°C

U=Qhc,mAΔTlm=(957.8+873.5)2 W(0.02 m2)(41.0°C)=1117 W/m2⋅C

Note that we used the average of two heat transfer rates in calculations.

(c) The fraction of heat loss and the heat transfer efficiency are

floss=Qh−QcQh=957.8−873.5957.8=0.088=8.8%η=QcQh=873.5957.8=0.912=91.2%

(d) The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(0.0172 kg/s)(4187 kJ/kg.°C)=72.02 W/°CCc=mccpc=(0.0258 kg/s)(4180 kJ/kg.°C)=107.8 W/°C

Therefore

Cmin=Ch=72.02 W/°C

which is the smaller of the two heat capacity rates. Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(72.02 W/°C)(71.5°C-19.7°C)=3731 W

The effectiveness of the heat exchanger is

ε=QQmax=(957.8+873.5)2 kW3731 kW=0.245=24.5%

One again we used the average heat transfer rate. We could have used the smaller or greater heat transfer rates in calculations. The NTU of the heat exchanger is determined from

NTU=UACmin=(1117 W/m2⋅C)(0.02 m2)72.02 W/°C=0.310

16-90 Water is heated by a hot water stream in a heat exchanger. The maximum outlet temperature of the cold water and the effectiveness of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Air

65C

0.8 kg/s

14C

0.35 kg/s

Properties The specific heats of water and air are given to be 4.18 and 1.0 kJ/kg.C.

Analysis The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(0.8 kg/s)(1.0 kJ/kg.°C)=0.8 kW/°CCc=mccpc=(0.35 kg/s)(4.18 kJ/kg.°C)=1.463 kW/°C

Therefore

Cmin=Ch=0.8 kW/°C

which is the smaller of the two heat capacity rates. Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(0.8 kW/°C)(65°C-14°C)=40.80 kW

The maximum outlet temperature of the cold fluid is determined to be

Qmax=Cc(Tc,out,max−Tc,in)Tc,out,max=Tc,in+QmaxCc=14°C+40.80 kW1.463 kW/°C=41.9°C

The actual rate of heat transfer and the effectiveness of the heat exchanger are

Q=Ch(Th,in−Th,out)=(0.8 kW/°C)(65°C-25°C)=32 kW

ε=QQmax=32 kW40.8 kW=0.784

16-91 Lake water is used to condense steam in a shell and tube heat exchanger. The outlet temperature of the water and the required tube length are to be determined.

Steam

60C

Lake water

20C

60C

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The properties of water are given in problem statement. The enthalpy of vaporization of water at 60C is 2359 kJ/kg (Table A-15).

Analysis (a) The rate of heat transfer is

Q=mhfg=(2.5 kg/s)(2359 kJ/kg)=5898 kW

The outlet temperature of water is determined from

Q=mccc(Tc,out−Tc,in)Tc,out=Tc,in+Qmccc=20°C+5898 kW(200 kg/s)(4.18 kJ/kg⋅°C)=27.1°C

(b) The Reynold number is

Re=4mNtubeπDμ=4(200 kg/s)(300)π(0.025 m)(8×10 -4kg/m⋅s)=42,440

which is greater than 10,000. Therefore, we have turbulent flow. We assume fully developed flow and evaluate the Nusselt number from

Nu=hDk=0.023Re0.8Pr0.4=0.023(42,440)0.8(6)0.4=237.2

Heat transfer coefficient on the inner surface of the tubes is

hi=kDNu=0.6 W/m.°C0.025 m(237.2)=5694 W/m2.°C

Disregarding the thermal resistance of the tube wall the overall heat transfer coefficient is determined from

U=11hi+1ho=115694+18500=3410 W/m2⋅°C

The logarithmic mean temperature difference is

ΔT1=Th,in−Tc,out=60°C−27.1°C=32.9°C

ΔT2=Th,out−Tc,in=60°C−20°C=40°C

ΔTlm=ΔT1−ΔT2lnΔT1ΔT2=32.9−40ln32.940=36.3°C

Noting that each tube makes two passes and taking the correction factor to be unity, the tube length per pass is determined to be

Q=UAFΔTlm→L=QU(πD)FΔTlm=5898 kW(3.410 kW/m2⋅C)2×300×π×0.025  m2(1)(36.3°C)=1.01 m

16-92 Air is heated by a hot water stream in a cross-flow heat exchanger. The maximum heat transfer rate and the outlet temperatures of the cold and hot fluid streams are to be determined.

Air

20C

3 kg/s

1 kg/s

70C

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The specific heats of water and air are given to be 4.19 and 1.005 kJ/kg.C.

Analysis The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(1 kg/s)(4190 J/kg.°C)=4190 W/°CCc=mccpc=(3 kg/s)(1005 J/kg.°C)=3015 W/°C

Therefore

Cmin=Cc=3015 W/°C

which is the smaller of the two heat capacity rates. Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(3015 W/°C)(70°C-20°C)=150,750 W=150.8 kW

The outlet temperatures of the cold and the hot streams in this limiting case are determined to be

Q=Cc(Tc,out−Tc,in)Tc,out=Tc,in+QCc=20°C+150.75 kW3.015 kW/°C=70°CQ=Ch(Th,in−Th,out)Th,out=Th,in−QCh=70°C−150.75 kW4.19 kW/°C=34.0°C

16-93 Hot oil is to be cooled by water in a heat exchanger. The mass flow rates and the inlet temperatures are given. The rate of heat transfer and the outlet temperatures are to be determined. 

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The thickness of the tube is negligible since it is thin-walled. 5 The overall heat transfer coefficient is constant and uniform.

Oil

160C

0.2 kg/s

Water

18C

0.1 kg/s

(12 tube passes)

Properties The specific heats of the water and oil are given to be 4.18 and 2.2 kJ/kg.C, respectively.

Analysis The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(0.2 kg/s)(2200 J/kg.°C)=440 W/°CCc=mccpc=(0.1 kg/s)(4180 J/kg.°C)=418 W/°C

Therefore,	Cmin=Cc=418 W/°C

and		c=CminCmax=418440=0.95

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(418 W/°C)(160°C-18°C)=59.36 kW

The heat transfer surface area is

As=n(πDL)=(12)(π)(0.018 m)(3 m)=2.04 m2

The NTU of this heat exchanger is

NTU=UAsCmin=(340 W/m2.°C)(2.04 m2)418 W/°C=1.659

Then the effectiveness of this heat exchanger corresponding to c = 0.95 and NTU = 1.659 is determined from Fig. 16-26d to be

 = 0.61

Then the actual rate of heat transfer becomes

Q=εQmax=(0.61)(59.36 kW)=36.2 kW

Finally, the outlet temperatures of the cold and hot fluid streams are determined to be

Q=Cc(Tc,out−Tc,in)Tc,out=Tc,in+QCc=18°C+36.2 kW0.418 kW°C=104.6°CQ=Ch(Th,in−Th,out)Th,out=Th,in−QCh=160°C−36.2 kW0.44 kW/°C =77.7°C

16-94 Inlet and outlet temperatures of the hot and cold fluids in a double-pipe heat exchanger are given. It is to be determined whether this is a parallel-flow or counter-flow heat exchanger and the effectiveness of it.

Analysis This is a counter-flow heat exchanger because in the parallel-flow heat exchangers the outlet temperature of the cold fluid (55C in this case) cannot exceed the outlet temperature of the hot fluid, which is (45C in this case). Noting that the mass flow rates of both hot and cold oil streams are the same, we have Cmin=Cmax. Then the effectiveness of this heat exchanger is determined from

ε=QQmax=Ch(Th,in−Th,out)Cmin(Th,in−Tc,in)=Ch(Th,in−Th,out)Ch(Th,in−Tc,in)=80°C−45°C80°C−20°C=0.583

16-95E Inlet and outlet temperatures of the hot and cold fluids in a double-pipe heat exchanger are given. It is to be determined the fluid, which has the smaller heat capacity rate and the effectiveness of the heat exchanger.

Analysis Hot water has the smaller heat capacity rate since it experiences a greater temperature change. The effectiveness of this heat exchanger is determined from

ε=QQmax=Ch(Th,in−Th,out)Cmin(Th,in−Tc,in)=Ch(Th,in−Th,out)Ch(Th,in−Tc,in)=190°F−100°F190°F−70°F=0.75

16-96 A chemical is heated by water in a heat exchanger. The mass flow rates and the inlet temperatures are given. The outlet temperatures of both fluids are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The thickness of the tube is negligible since tube is thin-walled. 5 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the water and chemical are given to be 4.18 and 1.8 kJ/kg.C, respectively.

Hot Water

110C

2 kg/s

Chemical

20C

3 kg/s

Analysis The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(2 kg/s)(4.18 kJ/kg.°C)=8.36 kW/°CCc=mccpc=(3 kg/s)(1.8 kJ/kg.°C)=5.40 kW/°C

Therefore,	Cmin=Cc=5.4 kW/°C

and		c=CminCmax=5.408.36=0.646

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(5.4 kW/°C)(110°C-20°C)=486 kW

The NTU of this heat exchanger is

NTU=UAsCmin=(1.2 kW/m2.°C)(7 m2)5.4 kW/°C=1.556

Then the effectiveness of this parallel-flow heat exchanger corresponding to c = 0.646 and NTU=1.556 is determined from

ε=1−exp[−NTU(1+c)]1+c=1−exp[−1.556(1+0.646)]1+0.646=0.56

Then the actual rate of heat transfer rate becomes

Q=εQmax=(0.56)(486 kW)=272.2 kW

Finally, the outlet temperatures of the cold and hot fluid streams are determined to be

Q=Cc(Tc,out−Tc,in)Tc,out=Tc,in+QCc=20°C+272.2 kW5.4 kW°C=70.4°CQ=Ch(Th,in−Th,out)Th,out=Th,in−QCh=110°C−272.2 kW8.36 kW/°C =77.4°C

16-97 EES Prob. 16-96 is reconsidered. The effects of the inlet temperatures of the chemical and the water on their outlet temperatures are to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_chemical_in=20 [C]

c_p_chemical=1.8 [kJ/kg-C]

m_dot_chemical=3 [kg/s]

T_w_in=110 [C]

m_dot_w=2 [kg/s]

c_p_w=4.18 [kJ/kg-C]

A=7 [m^2]

U=1.2 [kW/m^2-C]

"ANALYSIS"

"With EES, it is easier to solve this problem using LMTD method than NTU method. Below, we use LMTD method. Both methods give the same results."

DELTAT_1=T_w_in-T_chemical_in

DELTAT_2=T_w_out-T_chemical_out

DELTAT_lm=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

Q_dot=U*A*DELTAT_lm

Q_dot=m_dot_chemical*c_p_chemical*(T_chemical_out-T_chemical_in)

Q_dot=m_dot_w*c_p_w*(T_w_in-T_w_out)

| Tchemical, in [C] | Tchemical, out [C] |
| --- | --- |
| 10 | 66.06 |
| 12 | 66.94 |
| 14 | 67.82 |
| 16 | 68.7 |
| 18 | 69.58 |
| 20 | 70.45 |
| 22 | 71.33 |
| 24 | 72.21 |
| 26 | 73.09 |
| 28 | 73.97 |
| 30 | 74.85 |
| 32 | 75.73 |
| 34 | 76.61 |
| 36 | 77.48 |
| 38 | 78.36 |
| 40 | 79.24 |
| 42 | 80.12 |
| 44 | 81 |
| 46 | 81.88 |
| 48 | 82.76 |
| 50 | 83.64 |

| Tw, in [C] | Tw, out [C] |
| --- | --- |
| 80 | 58.27 |
| 85 | 61.46 |
| 90 | 64.65 |
| 95 | 67.84 |
| 100 | 71.03 |
| 105 | 74.22 |
| 110 | 77.41 |
| 115 | 80.6 |
| 120 | 83.79 |
| 125 | 86.98 |
| 130 | 90.17 |
| 135 | 93.36 |
| 140 | 96.55 |
| 145 | 99.74 |
| 150 | 102.9 |

16-98 Water is heated by hot air in a heat exchanger. The mass flow rates and the inlet temperatures are given. The heat transfer surface area of the heat exchanger on the water side is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the water and air are given to be 4.18 and 1.01kJ/kg.C, respectively.

Analysis The heat capacity rates of the hot and cold fluids are

Hot Air

100C

9 kg/s

Water

20C, 4 kg/s

Ch=mhcph=(4 kg/s)(4.18 kJ/kg.°C)=16.72 kW/°CCc=mccpc=(9 kg/s)(1.01 kJ/kg.°C)=9.09 kW/°C

Therefore,	Cmin=Cc=9.09 kW/°C

and		C=CminCmax=9.0916.72=0.544

Then the NTU of this heat exchanger corresponding to        c = 0.544 and  = 0.65 is determined from Fig. 16-26 to be

NTU = 1.5

Then the surface area of this heat exchanger becomes

NTU=UAsCminAs=NTU CminU=(1.5)(9.09 kW/°C)0.260 kW/m2.°C=52.4 m2

16-99 Water is heated by steam condensing in a condenser. The required length of the tube is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heat of the water is given to be 4.18 kJ/kg.C. The heat of vaporization of water at 120C is given to be 2203 kJ/kg.

80C

120C

120C

Steam

Water

17C

1.8 kg/s

Analysis (a) The temperature differences between the steam and the water at the two ends of the condenser are

ΔT1=Th,in−Tc,out=120°C−80°C=40°CΔT2=Th,out−Tc,in=120°C−17°C=103°C

The logarithmic mean temperature difference is

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=40−103ln(40103)=66.6°C

The rate of heat transfer is determined from

Q=mccpc(Tc,out−Tc,in)=(1.8 kg/s)(4.18 kJ/kg.°C)(80°C−17°C)=474.0 kW

The surface area of heat transfer is

Q=UAsΔTlmAs=QUΔTlm=474.0 kW0.7 kW/m2.°C)(66.6°C)=10.17 m2

The length of tube required then becomes

As=πDLL=AsπD=10.17 m2π(0.025 m)=129.5 m

(b) The maximum rate of heat transfer rate is

Qmax=Cmin(Th,in−Tc,in)=(1.8 kg/s)(4.18 kJ/kg.°C)(120°C-17°C)=775.0 kW

Then the effectiveness of this heat exchanger becomes

ε=QQmax=474 kW775 kW=0.612

The NTU of this heat exchanger is determined using the relation in Table 16-5 to be

NTU=−ln(1−ε)=−ln(1−0.612)=0.947

The surface area is

NTU=UAsCminAs=NTUCminU=(0.947)(1.8 kg/s)(4.18 kJ/kg.°C)0.7 kW/m2.°C=10.18 m2

Finally, the length of tube required is

As=πDLL=AsπD=10.18 m2π(0.025 m)=129.6 m

16-100 Ethanol is vaporized by hot oil in a double-pipe parallel-flow heat exchanger. The outlet temperature and the mass flow rate of oil are to be determined using the LMTD and NTU methods.

Ethanol

78C

0.03 kg/s

Oil

120C

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heat of oil is given to be 2.2 kJ/kg.C. The heat of vaporization of ethanol at 78C is given to be 846 kJ/kg.

Analysis (a) The rate of heat transfer is

Q=mhfg=(0.03 kg/s)(846 kJ/kg)=25.38 kW

The log mean temperature difference is

Q=UAsΔTlmΔTlm=QUAs=25,380 W(320 W/m2.°C)(6.2 m2)=12.8°C

The outlet temperature of the hot fluid can be determined as follows

ΔT1=Th,in−Tc,in=120°C−78°C=42°CΔT2=Th,out−Tc,out=Th,out−78°C

and	ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=42−(Th,out−78)ln[42(Th,out−78)]=12.8°C

whose solution is		Th,out=79.8°C

Then the mass flow rate of the hot oil becomes

Q=mcp(Th,in−Th,out)m=Qcp(Th,in−Th,out)=25,380 W(2200 J/kg.°C)(120°C−79.8°C)=0.287 kg/s

(b) The heat capacity rate C=mcp of a fluid condensing or evaporating in a heat exchanger is infinity, and thus C=CminCmax=0.

The effectiveness in this case is determined from ε=1−e−NTU

where   	NTU=UAsCmin=(320 W/m2.°C)(6.2 m2)(m, kg/s)(2200 J/kg.°C)

and 	Qmax=Cmin(Th,in−Tc,in)

ε=QQmax=Cmin(Th,in−Tc,in)Cmin(Th,in−Tc,in)=120−Th,out120−78

Q=Ch(Th,in−Th,out)=25,380 WQ=m×2200(120−Th,out)=25,380 W		(1)

Also	120−Th,out120−78=1−e−6.2×320m×2200				(2)

Solving (1) and (2) simultaneously gives

mh=0.287 kg/s   and   Th,out=79.8°C

16-101 Water is heated by solar-heated hot air in a heat exchanger. The mass flow rates and the inlet temperatures are given. The outlet temperatures of the water and the air are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the water and air are given to be 4.18 and 1.01 kJ/kg.C, respectively.

Hot Air

90C

0.3 kg/s

Cold Water

22C

0.1 kg/s

Analysis The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(0.3kg/s)(1010 J/kg.°C)=303 W/°CCc=mccpc=(0.1 kg/s)(4180 J/kg.°C)=418 W/°C

Therefore,  	Cmin=Cc=303 W/°C

and   		c=CminCmax=303418=0.725

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(303 W/°C)(90°C-22°C)=20,604 kW

The heat transfer surface area is

As=πDL=(π)(0.012 m)(12 m)=0.45 m2

Then the NTU of this heat exchanger becomes

NTU=UAsCmin=(80 W/m2.°C)(0.45 m2)303 W/°C=0.119

The effectiveness of this counter-flow heat exchanger corresponding to c = 0.725 and NTU = 0.119 is determined using the relation in Table 16-4 to be

ε=1−exp[−NTU(1−c)]1−cexp[−NTU(1−c)]=1−exp[−0.119(1−0.725)]1−0.725exp[−0.119(1−0.725)]=0.108

Then the actual rate of heat transfer becomes

Q=εQmax=(0.108)(20,604 W)=2225.2 W

Finally, the outlet temperatures of the cold and hot fluid streams are determined to be
	Q=Cc(Tc,out−Tc,in)Tc,out=Tc,in+QCc=22°C+2225.2 W418 W°C=27.3°CQ=Ch(Th,in−Th,out)Th,out=Th,in−QCh=90°C−2225.2 W303 W/°C =82.7°C

16-102 EES Prob. 16-101 is reconsidered. The effects of the mass flow rate of water and the tube length on the outlet temperatures of water and air are to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_air_in=90 [C]

m_dot_air=0.3 [kg/s]

c_p_air=1.01 [kJ/kg-C]

T_w_in=22 [C]

m_dot_w=0.1 [kg/s]

c_p_w=4.18 [kJ/kg-C]

U=0.080 [kW/m^2-C]

L=12 [m]

D=0.012 [m]

"ANALYSIS"

"With EES, it is easier to solve this problem using LMTD method than NTU method. Below, we use LMTD method. Both methods give the same results."

DELTAT_1=T_air_in-T_w_out

DELTAT_2=T_air_out-T_w_in

DELTAT_lm=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

A=pi*D*L

Q_dot=U*A*DELTAT_lm

Q_dot=m_dot_air*c_p_air*(T_air_in-T_air_out)

Q_dot=m_dot_w*c_p_w*(T_w_out-T_w_in)

| mw [kg/s] | Tw, out [C] | Tair, out [C] |
| --- | --- | --- |
| 0.05 | 32.27 | 82.92 |
| 0.1 | 27.34 | 82.64 |
| 0.15 | 25.6 | 82.54 |
| 0.2 | 24.72 | 82.49 |
| 0.25 | 24.19 | 82.46 |
| 0.3 | 23.83 | 82.44 |
| 0.35 | 23.57 | 82.43 |
| 0.4 | 23.37 | 82.42 |
| 0.45 | 23.22 | 82.41 |
| 0.5 | 23.1 | 82.4 |
| 0.55 | 23 | 82.4 |
| 0.6 | 22.92 | 82.39 |
| 0.65 | 22.85 | 82.39 |
| 0.7 | 22.79 | 82.39 |
| 0.75 | 22.74 | 82.38 |
| 0.8 | 22.69 | 82.38 |
| 0.85 | 22.65 | 82.38 |
| 0.9 | 22.61 | 82.38 |
| 0.95 | 22.58 | 82.38 |
| 1 | 22.55 | 82.37 |

| L [m] | Tw, out [C] | Tair, out [C] |
| --- | --- | --- |
| 5 | 24.35 | 86.76 |
| 6 | 24.8 | 86.14 |
| 7 | 25.24 | 85.53 |
| 8 | 25.67 | 84.93 |
| 9 | 26.1 | 84.35 |
| 10 | 26.52 | 83.77 |
| 11 | 26.93 | 83.2 |
| 12 | 27.34 | 82.64 |
| 13 | 27.74 | 82.09 |
| 14 | 28.13 | 81.54 |
| 15 | 28.52 | 81.01 |
| 16 | 28.9 | 80.48 |
| 17 | 29.28 | 79.96 |
| 18 | 29.65 | 79.45 |
| 19 | 30.01 | 78.95 |
| 20 | 30.37 | 78.45 |
| 21 | 30.73 | 77.96 |
| 22 | 31.08 | 77.48 |
| 23 | 31.42 | 77 |
| 24 | 31.76 | 76.53 |
| 25 | 32.1 | 76.07 |

16-103E Oil is cooled by water in a double-pipe heat exchanger. The overall heat transfer coefficient of this heat exchanger is to be determined using both the LMTD and NTU methods.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The thickness of the tube is negligible since it is thin-walled.

Properties The specific heats of the water and oil are given to be 1.0 and 0.525 Btu/lbm.F, respectively.

Analysis (a) The rate of heat transfer is

Q=mhcph(Th,in−Th,out)=(5 lbm/s)(0.525 Btu/lbm.°F)(300−105°F)=511.9 Btu/s

The outlet temperature of the cold fluid is

Q=mccpc(Tc,out−Tc,in)Tc,out=Tc,in+Qmccpc=70°F+511.9 Btu/s(3 lbm/s)(1.0 Btu/lbm.°F)=240.6°F

Hot Oil

300F

5 lbm/s

Cold Water

70F

3 lbm/s

105F

The temperature differences between the two fluids at the two ends of the heat exchanger are

ΔT1=Th,in−Tc,out=300°F−240.6°F=59.4°FΔT2=Th,out−Tc,in=105°F−70°F=35°F

The logarithmic mean temperature difference is

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=59.4−35ln(59.4/35)=46.1°F

Then the overall heat transfer coefficient becomes

Q=UAsΔTlmU=QAsΔTlm=511.9 Btu/sπ(512 m)(200 ft)(46.1°F)=0.0424 Btu/s.ft2.°F

(b) The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(5 lbm/s)(0.525 Btu/lbm.°F)=2.625 Btu/s.°FCc=mccpc=(3 lbm/s)(1.0 Btu/lbm.°F)=3.0 Btu/s.°F

Therefore,   Cmin=Ch=2.625 Btu/s.°F   and   c=CminCmax=2.6253.0=0.875

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(2.625 Btu/s.°F)(300°F-70°F)=603.75 Btu/s

The actual rate of heat transfer and the effectiveness are

Q=Ch(Th,in−Th,out)=(2.625 Btu/s.°F)(300°F-105°F)=511.9 Btu/s

ε=QQmax=511.9603.75=0.85

The NTU of this heat exchanger is determined using the relation in Table 16-5 to be

NTU=1c−1lnε−1εc−1=10.875−1ln0.85−10.85×0.875−1=4.28

The heat transfer surface area of the heat exchanger is

As=πDL=π(512 ft)(200 ft)=261.8 ft2

and	NTU=UAsCminU=NTUCminAs=(4.28)(2.625 Btu/s.°F)261.8 ft2=0.0429 Btu/s.ft2.°F

16-104 Cold water is heated by hot water in a heat exchanger. The net rate of heat transfer and the heat transfer surface area of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform. 5 The thickness of the tube is negligible.

Properties The specific heats of the cold and hot water are given to be 4.18 and 4.19 kJ/kg.C, respectively.

Hot Water

100C

3 kg/s

Cold Water

15C

0.25 kg/s

45C

Analysis The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(0.25 kg/s)(4180 J/kg.°C)=1045 W/°CCc=mccpc=(3 kg/s)(4190 J/kg.°C)=12,570 W/°C

Therefore,	Cmin=Cc=1045 W/°C

and		c=CminCmax=104512,570=0.083

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(1045 W/°C)(100°C-15°C)=88,825 W

The actual rate of heat transfer is

Q=Ch(Th,in−Th,out)=(1045 W/°C)(45°C−15°C)=31,350 W

Then the effectiveness of this heat exchanger becomes

ε=QQmax=31,35088,825=0.35

The NTU of this heat exchanger is determined using the relation in Table 16-5 to be

NTU=1c−1lnε−1εc−1=10.083−1ln0.35−10.35×0.083−1=0.438

Then the surface area of the heat exchanger is determined from

NTU=UACminA=NTUCminU=(0.438)(1045 W/°C)950 W/m2.°C=0.482 m2

16-105 EES Prob. 16-104 is reconsidered. The effects of the inlet temperature of hot water and the heat transfer coefficient on the rate of heat transfer and the surface area are to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

T_cw_in=15 [C]

T_cw_out=45 [C]

m_dot_cw=0.25 [kg/s]

c_p_cw=4.18 [kJ/kg-C]

T_hw_in=100 [C]

m_dot_hw=3 [kg/s]

c_p_hw=4.19 [kJ/kg-C]

U=0.95 [kW/m^2-C]

"ANALYSIS"

"With EES, it is easier to solve this problem using LMTD method than NTU method. Below, we use LMTD method. Both methods give the same results."

DELTAT_1=T_hw_in-T_cw_out

DELTAT_2=T_hw_out-T_cw_in

DELTAT_lm=(DELTAT_1-DELTAT_2)/ln(DELTAT_1/DELTAT_2)

Q_dot=U*A*DELTAT_lm

Q_dot=m_dot_hw*c_p_hw*(T_hw_in-T_hw_out)

Q_dot=m_dot_cw*c_p_cw*(T_cw_out-T_cw_in)

| Thw, in [C] | Q [kW] | A [m2] |
| --- | --- | --- |
| 60 | 31.35 | 1.25 |
| 65 | 31.35 | 1.038 |
| 70 | 31.35 | 0.8903 |
| 75 | 31.35 | 0.7807 |
| 80 | 31.35 | 0.6957 |
| 85 | 31.35 | 0.6279 |
| 90 | 31.35 | 0.5723 |
| 95 | 31.35 | 0.5259 |
| 100 | 31.35 | 0.4865 |
| 105 | 31.35 | 0.4527 |
| 110 | 31.35 | 0.4234 |
| 115 | 31.35 | 0.3976 |
| 120 | 31.35 | 0.3748 |

| U [kW/m2-C] | Q [kW] | A [m2] |
| --- | --- | --- |
| 0.75 | 31.35 | 0.6163 |
| 0.8 | 31.35 | 0.5778 |
| 0.85 | 31.35 | 0.5438 |
| 0.9 | 31.35 | 0.5136 |
| 0.95 | 31.35 | 0.4865 |
| 1 | 31.35 | 0.4622 |
| 1.05 | 31.35 | 0.4402 |
| 1.1 | 31.35 | 0.4202 |
| 1.15 | 31.35 | 0.4019 |
| 1.2 | 31.35 | 0.3852 |
| 1.25 | 31.35 | 0.3698 |

16-106 Glycerin is heated by ethylene glycol in a heat exchanger. Mass flow rates and inlet temperatures are given. The rate of heat transfer and the outlet temperatures are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform. 5 The thickness of the tube is negligible.

Properties The specific heats of the glycerin and ethylene glycol are given to be 2.4 and 2.5 kJ/kg.C, respectively.

Ethylene

60C

0.3 kg/s

Glycerin

20C

0.3 kg/s

Analysis (a) The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(0.3 kg/s)(2400 J/kg.°C)=720 W/°CCc=mccpc=(0.3 kg/s)(2500 J/kg.°C)=750 W/°C

Therefore,	Cmin=Ch=720 W/°C

and		c=CminCmax=720750=0.96

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(720 W/°C)(60°C−20°C)=28.8 kW

The NTU of this heat exchanger is

NTU=UAsCmin=(380 W/m2.°C)(5.3 m2)720 W/°C=2.797

Effectiveness of this heat exchanger corresponding to c = 0.96 and NTU = 2.797 is determined using the proper relation in Table 16-4

ε=1−exp[−NTU(1+c)]1+c=1−exp[−2.797(1+0.96)]1+0.96=0.508

Then the actual rate of heat transfer becomes

Q=εQmax=(0.508)(28.8 kW)=14.63 kW

(b) Finally, the outlet temperatures of the cold and the hot fluid streams are determined from
	Q=Cc(Tc,out−Tc,in)Tc,out=Tc,in+QCc=20°C+14.63 kW0.72 kW°C=40.3°CQ=Ch(Th,in−Th,out)Th,out=Th,in−QCh=60°C−14.63 kW0.75 kW/°C =40.5°C

16-107 Water is heated by hot air in a cross-flow heat exchanger. Mass flow rates and inlet temperatures are given. The rate of heat transfer and the outlet temperatures are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform. 5 The thickness of the tube is negligible.

Properties The specific heats of the water and air are given to be 4.18 and 1.01 kJ/kg.C, respectively.

Analysis The mass flow rates of the hot and the cold fluids are

mc=ρVAc=(1000 kg/m3)(3 m/s)[80π(0.03 m)2/4]=169.6 kg/s

Hot Air

130C

105 kPa

12 m/s

Water

18C, 3 m/s

1 m

1 m

1 m

ρair=PRT=105 kPa(0.287 kPa.m3/kg.K)×(130+273 K)=0.908 kg/m3

mh=ρVAc=(0.908 kg/m3)(12 m/s)(1 m)2=10.90 kg/s

The heat transfer surface area and the heat capacity rates are

As=nπDL=80π(0.03 m)(1 m)=7.540 m2

Cc=mccpc=(169.6 kg/s)(4.18 kJ/kg.°C)=708.9 kW/°CCh=mhcph=(10.9 kg/s)(1.010 kJ/kg.°C)=11.01 kW/°C

Therefore, Cmin=Cc=11.01 kW/°C  and   c=CminCmax=11.01708.9=0.01553

Qmax=Cmin(Th,in−Tc,in)=(11.01 kW/°C)(130°C−18°C)=1233 kW

The NTU of this heat exchanger is

NTU=UAsCmin=(130 W/m2.°C)(7.540 m2)11,010 W/°C=0.08903

Noting that this heat exchanger involves mixed cross-flow, the fluid with Cmin is mixed, Cmax unmixed, effectiveness of this heat exchanger corresponding to c = 0.01553 and NTU =0.08903 is determined using the proper relation in Table 16-4 to be

ε=1−exp−1c(1−e−cNTU)=1−exp−10.01553(1−e−0.01553×0.08903)=0.08513

Then the actual rate of heat transfer becomes

Q=εQmax=(0.08513)(1233 kW)=105.0 kW

Finally, the outlet temperatures of the cold and the hot fluid streams are determined from

Q=Cc(Tc,out−Tc,in)Tc,out=Tc,in+QCc=18°C+105.0 kW708.9 kW°C=18.15°CQ=Ch(Th,in−Th,out)Th,out=Th,in−QCh=130°C−105.0 kW11.01 kW/°C =120.5°C

16-108 CD EES Ethyl alcohol is heated by water in a shell-and-tube heat exchanger. The heat transfer surface area of the heat exchanger is to be determined using both the LMTD and NTU methods.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the ethyl alcohol and water are given to be 2.67 and 4.19 kJ/kg.C, respectively.

Water

95C

Alcohol

25C

2.1 kg/s

70C

2-shell pass

8 tube passes

60C

Analysis (a) The temperature differences between the two fluids at the two ends of the heat exchanger are

ΔT1=Th,in−Tc,out=95°C−70°C=25°CΔT2=Th,out−Tc,in=60°C−25°C=35°C

The logarithmic mean temperature difference and the correction factor are

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=25−35ln(25/35)=29.7°C

P=t2−t1T1−t1=70−2595−25=0.64F=0.93

The rate of heat transfer is determined from

Q=mccpc(Tc,out−Tc,in)=(2.1 kg/s)(2.67 kJ/kg.°C)(70°C−25°C)=252.3 kW

The surface area of heat transfer is

Q=UAsΔTlmAs=QUFΔTlm=252.3 kW0.8 kW/m2.°C)(0.93)(29.7°C)=11.4 m2

(b) The rate of heat transfer is

Q=mccpc(Tc,out−Tc,in)=(2.1 kg/s)(2.67 kJ/kg.°C)(70°C−25°C)=252.3 kW

The mass flow rate of the hot fluid is

Q=mhcph(Th,in−Th,out)→mh=Qcph(Th,in−Th,out)=252.3 kW(4.19 kJ/kg.°C)(95°C−60°C)=1.72 kg/s

The heat capacity rates of the hot and the cold fluids are

Ch=mhcph=(1.72 kg/s)(4.19 kJ/kg.°C)=7.21 kW/°CCc=mccpc=(2.1 kg/s)(2.67 kJ/kg.°C)=5.61 kW/°C

Therefore,   Cmin=Cc=5.61 W/°C  and   c=CminCmax=5.617.21=0.78

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(5.61 W/°C)(95°C−25°C)=392.7 kW

The effectiveness of this heat exchanger is		ε=QQmax=252.3392.7=0.64

The NTU of this heat exchanger corresponding to this emissivity and c = 0.78 is determined from Fig. 16-26d to be NTU = 1.7. Then the surface area of heat exchanger is determined to be

NTU=UAsCminAs=NTUCminU=(1.7)(5.61 kW/°C)0.8 kW/m2.°C=11.9 m2

The small difference between the two results is due to the reading error of the chart.

16-109 Steam is condensed by cooling water in a shell-and-tube heat exchanger. The rate of heat transfer and the rate of condensation of steam are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform. 5 The thickness of the tube is negligible.

Properties The specific heat of the water is given to be 4.18 kJ/kg.C. The heat of condensation of steam at 30C is given to be 2430 kJ/kg.

Analysis (a) The heat capacity rate of a fluid condensing in a heat exchanger is infinity. Therefore,

Cmin=Cc=mccpc=(0.5 kg/s)(4.18 kJ/kg.°C)=2.09 kW/°C

and	 c = 0

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(2.09 kW/°C)(30°C−15°C)=31.35 kW

Steam

30C

15C

Water

1800 kg/h

30C

and

As=8nπDL=8×50π(0.015 m)(2 m)=37.7 m2

The NTU of this heat exchanger

NTU=UAsCmin=(3 kW/m2.°C)(37.7 m2)2.09 kW/°C=54.11

Then the effectiveness of this heat exchanger corresponding to c = 0 and NTU = 54.11 is determined using the proper relation in Table 16-5

ε=1−exp(−NTU)=1−exp(−54.11)=1

Then the actual heat transfer rate becomes

Q=εQmax=(1)(31.35 kW)=31.35 kW

(b) Finally, the rate of condensation of the steam is determined from

Q=mhfgm=Qhfg=31.35 kJ/s2430 kJ/kg=0.0129 kg/s

16-110 EES Prob. 16-109 is reconsidered. The effects of the condensing steam temperature and the tube diameter on the rate of heat transfer and the rate of condensation of steam are to be investigated.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

N_pass=8

N_tube=50

T_steam=30 [C]

h_fg_steam=2430 [kJ/kg]

T_w_in=15 [C]

m_dot_w=1800[kg/h]*Convert(kg/h, kg/s)

c_p_w=4.18 [kJ/kg-C]

D=1.5 [cm]

L=2 [m]

U=3 [kW/m^2-C]

"ANALYSIS"

"With EES, it is easier to solve this problem using LMTD method than NTU method. Below, we use NTU method. Both methods give the same results."

C_min=m_dot_w*c_p_w

c=0 "since the heat capacity rate of a fluid condensing is infinity"

Q_dot_max=C_min*(T_steam-T_w_in)

A=N_pass*N_tube*pi*D*L*Convert(cm, m)

NTU=(U*A)/C_min

epsilon=1-exp(-NTU) "from Table 16-4 of the text with c=0"

Q_dot=epsilon*Q_dot_max

Q_dot=m_dot_cond*h_fg_steam

| Tsteam [C] | Q [kW] | mcond [kg/s] |
| --- | --- | --- |
| 20 | 10.45 | 0.0043 |
| 22.5 | 15.68 | 0.006451 |
| 25 | 20.9 | 0.008601 |
| 27.5 | 26.12 | 0.01075 |
| 30 | 31.35 | 0.0129 |
| 32.5 | 36.58 | 0.01505 |
| 35 | 41.8 | 0.0172 |
| 37.5 | 47.03 | 0.01935 |
| 40 | 52.25 | 0.0215 |
| 42.5 | 57.47 | 0.02365 |
| 45 | 62.7 | 0.0258 |
| 47.5 | 67.93 | 0.02795 |
| 50 | 73.15 | 0.0301 |
| 52.5 | 78.38 | 0.03225 |
| 55 | 83.6 | 0.0344 |
| 57.5 | 88.82 | 0.03655 |
| 60 | 94.05 | 0.0387 |
| 62.5 | 99.27 | 0.04085 |
| 65 | 104.5 | 0.043 |
| 67.5 | 109.7 | 0.04515 |
| 70 | 114.9 | 0.0473 |

| D [cm] | Q [kW] | mcond [kg/s] |
| --- | --- | --- |
| 1 | 31.35 | 0.0129 |
| 1.05 | 31.35 | 0.0129 |
| 1.1 | 31.35 | 0.0129 |
| 1.15 | 31.35 | 0.0129 |
| 1.2 | 31.35 | 0.0129 |
| 1.25 | 31.35 | 0.0129 |
| 1.3 | 31.35 | 0.0129 |
| 1.35 | 31.35 | 0.0129 |
| 1.4 | 31.35 | 0.0129 |
| 1.45 | 31.35 | 0.0129 |
| 1.5 | 31.35 | 0.0129 |
| 1.55 | 31.35 | 0.0129 |
| 1.6 | 31.35 | 0.0129 |
| 1.65 | 31.35 | 0.0129 |
| 1.7 | 31.35 | 0.0129 |
| 1.75 | 31.35 | 0.0129 |
| 1.8 | 31.35 | 0.0129 |
| 1.85 | 31.35 | 0.0129 |
| 1.9 | 31.35 | 0.0129 |
| 1.95 | 31.35 | 0.0129 |
| 2 | 31.35 | 0.0129 |

16-111 Cold water is heated by hot oil in a shell-and-tube heat exchanger. The rate of heat transfer is to be determined using both the LMTD and NTU methods.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the water and oil are given to be 4.18 and 2.2 kJ/kg.C, respectively.

Analysis (a) The LMTD method in this case involves iterations, which involves the following steps:

1) Choose Th,out

Hot oil

200C

3 kg/s

Water

14C

3 kg/s

(20 tube passes)

2) Calculate Q from Q=mhcp(Th,out−Th,in)

3) Calculate Th,out from Q=mhcp(Th,out−Th,in)

4) Calculate ΔTlm,CF

5) Calculate Q from Q=UAsFΔTlm,CF

6) Compare to the Q calculated at step 2, and repeat until reaching the same result

Result: 651 kW

(b) The heat capacity rates of the hot and the cold fluids are

Ch=mhcph=(3 kg/s)(2.2 kJ/kg.°C)=6.6 kW/°CCc=mccpc=(3 kg/s)(4.18 kJ/kg.°C)=12.54 kW/°C

Therefore,   Cmin=Ch=6.6 kW/°C  and   c=CminCmax=6.612.54=0.53

Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(6.6 kW/°C)(200°C−14°C)=1228 kW

The NTU of this heat exchanger is

NTU=UAsCmin=(0.3 kW/m2.°C)(20 m2)6.6 kW/°C=0.91

Then the effectiveness of this heat exchanger corresponding to c = 0.53 and NTU = 0.91 is determined from Fig. 16-26d to be

ε=0.53

The actual rate of heat transfer then becomes

Q=εQmax=(0.53)(1228 kW)=651 kW

Selection of the Heat Exchangers

16-112C 1) Calculate heat transfer rate, 2) select a suitable type of heat exchanger, 3) select a suitable type of cooling fluid, and its temperature range, 4) calculate or select U, and 5) calculate the size (surface area) of heat exchanger

16-113C The first thing we need to do is determine the life expectancy of the system. Then we need to evaluate how much the larger will save in pumping cost, and compare it to the initial cost difference of the two units. If the larger system saves more than the cost difference in its lifetime, it should be preferred.

16-114C In the case of automotive and aerospace industry, where weight and size considerations are important, and in situations where the space availability is limited, we choose the smaller heat exchanger.

16-115 Oil is to be cooled by water in a heat exchanger. The heat transfer rating of the heat exchanger is to be determined and a suitable type is to be proposed.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible.

Properties The specific heat of the oil is given to be 2.2 kJ/kg.C.

Analysis The heat transfer rate of this heat exchanger is

Q=mccpc(Tc,out−Tc,in)=(13 kg/s)(2.2 kJ/kg.°C)(120°C−50°C)=2002 kW

We propose a compact heat exchanger (like the car radiator) if air cooling is to be used, or a tube-and-shell or plate heat exchanger if water cooling is to be used.

3-116 Water is to be heated by steam in a shell-and-tube process heater. The number of tube passes need to be used is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible.

Steam

20C

Water

90C

Properties The specific heat of the water is given to be 4.19 kJ/kg.C.

Analysis The mass flow rate of the water is

Q=mccpc(Tc,out−Tc,in)m=Qcpc(Tc,out−Tc,in)600 kW(4.19 kJ/kg.°C)(90°C−20°C)2.046 kg/s

The total cross-section area of the tubes corresponding to this mass flow rate is

m=ρVAc→Ac=mρV=2.046 kg/s(1000 kg/m3)(3 m/s)=6.82×10−4 m2

Then the number of tubes that need to be used becomes

As=nπD24n=4AsπD2=4(6.82×10−4 m2)π(0.01 m)2=8.68≃9

Therefore, we need to use at least 9 tubes entering the heat exchanger.

16-117 EES Prob. 16-116 is reconsidered. The number of tube passes as a function of water velocity is to be plotted.

Analysis The problem is solved using EES, and the solution is given below.

"GIVEN"

c_p_w=4.19 [kJ/kg-C]

T_w_in=20 [C]

T_w_out=90 [C]

Q_dot=600 [kW]

D=0.01 [m]

Vel=3 [m/s]

"PROPERTIES"

rho=density(water, T=T_ave, P=100)

T_ave=1/2*(T_w_in+T_w_out)

"ANALYSIS"

Q_dot=m_dot_w*c_p_w*(T_w_out-T_w_in)

m_dot_w=rho*A_c*Vel

A_c=N_pass*pi*D^2/4

| Vel [m/s] | Npass |
| --- | --- |
| 1 | 26.42 |
| 1.5 | 17.62 |
| 2 | 13.21 |
| 2.5 | 10.57 |
| 3 | 8.808 |
| 3.5 | 7.55 |
| 4 | 6.606 |
| 4.5 | 5.872 |
| 5 | 5.285 |
| 5.5 | 4.804 |
| 6 | 4.404 |
| 6.5 | 4.065 |
| 7 | 3.775 |
| 7.5 | 3.523 |
| 8 | 3.303 |

16-118 Cooling water is used to condense the steam in a power plant. The total length of the tubes required in the condenser is to be determined and a suitable HX type is to be proposed.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Steam

30C

18C

Water

30C

26C

Properties The specific heat of the water is given to be 4.18 kJ/kg.C. The heat of condensation of steam at 30C is given to be 2431 kJ/kg.

Analysis The temperature differences between the steam and the water at the two ends of condenser are

ΔT1=Th,in−Tc,out=30°C−26°C=4°CΔT2=Th,out−Tc,in=30°C−18°C=12°C

and the logarithmic mean temperature difference is

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=4−12ln4/12=7.28°C

The heat transfer surface area is

Q=UAsΔTlmAs=QUΔTlm=500×106 W(3500 W/m2.°C)(7.28°C)=1.96×104 m2

The total length of the tubes required in this condenser then becomes

As=πDLL=AsπD=1.96×104 m2π(0.02 m)=3.123×105 m=312.3 km

A multi-pass shell-and-tube heat exchanger is suitable in this case.

16-119 Cold water is heated by hot water in a heat exchanger. The net rate of heat transfer and the heat transfer surface area of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Steam

30C

18C

Water

30C

26C

Properties The specific heats of the cold and hot water are given to be 4.18 and 4.19 kJ/kg.C, respectively.

Analysis The temperature differences between the steam and the water at the two ends of condenser are

ΔT1=Th,in−Tc,out=30°C−26°C=4°CΔT2=Th,out−Tc,in=30°C−18°C=12°C

and the logarithmic mean temperature difference is

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=4−12ln(4/12)=7.28°C

The heat transfer surface area is

Q=UAsΔTlmAs=QUΔTlm=50×106 W(3500 W/m2.°C)(7.28°C)=1962 m2

The total length of the tubes required in this condenser then becomes

As=πDLL=AsπD=1962 m2π(0.02 m)=31,231 m=31.23 km

A multi-pass shell-and-tube heat exchanger is suitable in this case.

Review Problems

16-120 The inlet conditions of hot and cold fluid streams in a heat exchanger are given. The outlet temperatures of both streams are to be determined using LMTD and the effectiveness-NTU methods.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The specific heats of hot and cold fluid streams are given to be 2.0 and 4.2 kJ/kg.C, respectively.

Analysis (a) The rate of heat transfer can be expressed as

Q=mcp(Th,in−Th,out)=(27003600 kg/s)(2.0 kJ/kg.°C)(120−Th,out)=1.5(120−Th,out)	(1)

Q=mcp(Tc,out−Tc,in)=(18003600 kg/s)(4.2 kJ/kg.°C)(Tc,out−20)=2.1(Tc,out−20)	  	(2)

The heat transfer can also be expressed using the logarithmic mean temperature difference as

20C

1800 kg/h

120C

2700 kg/h

Th,out

Tc,out

ΔT1=Th,in−Tc,in=120°C−20°C=100°C

ΔT2=Th,out−Tc,out

ΔTlm=ΔT1−ΔT2lnΔT1ΔT2=100−(Th,out−Tc,out)ln100Th,out−Tc,out

Q=UAΔTlm=Qhc,mAΔTlm(2.0 kW/m2⋅°C)(0.50 m2)100−(Th,out−Tc,out)ln100Th,out−Tc,out=100−(Th,out−Tc,out)ln100Th,out−Tc,out 		(3)

Now we have three expressions for heat transfer with three unknowns: Q, Th,out, Tc,out. Solving them using an equation solver such as EES, we obtain

Q=59.6 kWTh,out=80.3°CTc,out=48.4°C

(b) The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(2700/3600 kg/s)(2.0 kJ/kg.°C)=1.5 kW/°CCc=mccpc=(1800/3600 kg/s)(4.2 kJ/kg.°C)=2.1 kW/°C

Therefore

Cmin=Ch=1.5 kW/°C

which is the smaller of the two heat capacity rates. The heat capacity ratio and the NTU are

c=CminCmax=1.52.1=0.714

NTU=UACmin=(2.0 kW/m2⋅C)(0.50 m2)1.5 kW/°C=0.667

The effectiveness of this parallel-flow heat exchanger is

ε=1−exp−NTU(1+c)1+c=1−exp−(0.667)(1+0.714)1+0.714=0.397

The maximum heat transfer rate is

Qmax=Cmin(Th,in−Tc,in)=(1.5 kW/°C)(120°C−20°C)=150 kW

The actual heat transfer rate is

Q=εQmax=(0.397)(150)=59.6 kW

Then the outlet temperatures are determined to be

Q=Cc(Tc,out−Tc,in)Tc,out=Tc,in+QCc=20°C+59.6 kW2.1 kW/°C=48.4°C

Q=Ch(Th,in−Th,out)Th,out=Th,in−QCh=120°C-59.6 kW1.5 kW/°C=80.3°C

Discussion The results obtained by two methods are same as expected. However, the effectiveness-NTU method is easier for this type of problems.

16-121 Water is used to cool a process stream in a shell and tube heat exchanger. The tube length is to be determined for one tube pass and four tube pass cases.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The properties of process stream and water are given in problem statement.

Analysis (a) The rate of heat transfer is

Q=mhch(Th,in−Th,out)=(47 kg/s)(3.5 kJ/kg⋅°C)(160−100)°C=9870 kW

The outlet temperature of water is determined from

Water

10C

Process stream

160C

100C

Q=mccc(Tc,out−Tc,in)Tc,out=Tc,in+QmcCc=10°C+9870 kW(66 kg/s)(4.18 kJ/kg⋅°C)=45.8°C

The logarithmic mean temperature difference is

ΔT1=Th,in−Tc,out=160°C−45.8°C=114.2°C

ΔT2=Th,out−Tc,in=100°C−10°C=90°C

ΔTlm=ΔT1−ΔT2lnΔT1ΔT2=114.2−90ln114.290=101.6°C

The Reynolds number is

V=mρA=mNtubeρπD24=(47 kg/s)(100)(950 kg/m3)π(0.025 m)24=1.008 m/sRe=VDρμ=(1.008 m/s)(0.025 m)(950 kg/m3)0.002 kg/m⋅s=11,968

which is greater than 10,000. Therefore, we have turbulent flow. We assume fully developed flow and evaluate the Nusselt number from

Pr=μcpk=(0.002 kg/m⋅s)(3500 J/kg⋅°C)0.50 W/m⋅°C=14Nu=hDk=0.023Re0.8Pr0.3=0.023(11,968)0.8(14)0.3=92.9

Heat transfer coefficient on the inner surface of the tubes is

hi=kDNu=0.50 W/m.°C0.025 m(92.9)=1858 W/m2.°C

Disregarding the thermal resistance of the tube wall the overall heat transfer coefficient is determined from

U=11hi+1ho=111858+14000=1269 W/m2⋅°C

The correction factor for one shell pass and one tube pass heat exchanger is F = 1. The tube length is determined to be

Q=UAFΔTlm9870 kW=(1.269 kW/m2⋅C)100π(0.025 m)L(1)(101.6°C)L=9.75 m

(b) For 1 shell pass and 4 tube passes, there are 100/4=25 tubes per pass and this will increase the velocity fourfold. We repeat the calculations for this case as follows:

V=4×1.008=4.032 m/sRe=4×11,968=47,872

Nu=hDk=0.023Re0.8Pr0.3=0.023(47,872)0.8(14)0.3=281.6

hi=kDNu=0.50 W/m.°C0.025 m(281.6)=5632 W/m2.°C

U=11hi+1ho=115632+14000=2339 W/m2⋅°C

The correction factor is determined from Fig. 16-18:

P=t2−t1T1−t1=100−16010−160=0.4F=0.96

The tube length is determined to be

Q=UAFΔTlm9870 kW=(2.339 kW/m2⋅C)100π(0.025 m)L(0.96)(101.6°C)L=5.51 m

16-122 A hydrocarbon stream is heated by a water stream in a 2-shell passes and 4-tube passes heat exchanger. The rate of heat transfer and the mass flow rates of both fluid streams and the fouling factor after usage are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The specific heat of HC is given to be 2 kJ/kg.C. The specific heat of water is taken to be 4.18 kJ/kg.C.

Analysis (a) The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

Water

80C

HC

20C

50C

2 shell passes

4 tube passes

40C

ΔT1=Th,in−Tc,out=80°C−50°C=30°CΔT2=Th,out−Tc,in=40°C−20°C=20°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=30−20ln(3020)=24.66°C

P=t2−t1T1−t1=50−2080−20=0.5F=0.90 (Fig. 16-18)

The overall heat transfer coefficient of the heat exchanger is

U=11hi+1ho=111600+12500=975.6 W/m2⋅°C

The rate of heat transfer in this heat exchanger is

Q=UAsFΔTlm,CF=(975.6 W/m2.°C)160π(0.02 m)(1.5 m)(0.90)(24.66°C)=3.265×105 W=326.5 kW

The mass flow rates of fluid streams are

mc=Qcp(Tout−Tin)=326.5 kW(2.0 kJ/kg.°C)(50°C−20°C)=5.44 kg/smh=Qcp(Tin−Tout)=326.5 kW(4.18 kJ/kg.°C)(80°C−40°C)=1.95 kg/s

(b) The rate of heat transfer in this case is

Q=[mcp(Tout−Tin)]c=(5.44 kg/s)(2.0 kJ/kg.°C)(45°C−20°C)=272 kW

This corresponds to a 17% decrease in heat transfer. The outlet temperature of the hot fluid is

Q=[mcp(Tin−Tout)]h272 kW=(1.95 kg/s)(4.18 kJ/kg.°C)(80°C−Th,out)Th,out=46.6°C

The logarithmic temperature difference is

ΔT1=Th,in−Tc,out=80°C−45°C=35°CΔT2=Th,out−Tc,in=46.6°C−20°C=26.6°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=35−26.6ln(3526.6)=30.61°C

P=t2−t1T1−t1=45−2080−20=0.42F=0.97 (Fig. 16-18)

The overall heat transfer coefficient is

Q=UAsFΔTlm,CF272,000 W=U160π(0.02 m)(1.5 m)(0.97)(30.61°C)U=607.5 W/m2.°C

The fouling factor is determined from

Rf=1Udirty−1Uclean=1607.5−1975.6=6.21×10−4 m2⋅°C/W

16-123 Hot water is cooled by cold water in a 1-shell pass and 2-tube passes heat exchanger. The mass flow rates of both fluid streams are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant. 5 There is no fouling.

Properties The specific heats of both cold and hot water streams are taken to be 4.18 kJ/kg.C.

Water

7C

Water

60C

36C

1 shell pass

2 tube passes

31C

Analysis The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=60°C−31°C=29°CΔT2=Th,out−Tc,in=36°C−7°C=29°C

Since ΔT1=ΔT2, we have ΔTlm,CF=29°C

P=t2−t1T1−t1=31−607−60=0.45F=0.88 (Fig. 16-18)

The rate of heat transfer in this heat exchanger is

Q=UAsFΔTlm,CF=(950 W/m2.°C)(15 m2)(0.88)(29°C)=3.64×105 W=364 kW

The mass flow rates of fluid streams are

mc=Qcp(Tout−Tin)=364 kW(4.18 kJ/kg.°C)(60°C−36°C)=3.63 kg/smh=Qcp(Tin−Tout)=364 kW(4.18 kJ/kg.°C)(31°C−7°C)=3.63 kg/s

16-124 Hot oil is cooled by water in a multi-pass shell-and-tube heat exchanger. The overall heat transfer coefficient based on the inner surface is to be determined.

Assumptions 1 Water flow is fully developed. 2 Properties of the water are constant.

Properties The properties of water at 25C are (Table A-15)

Outer surface

D0, A0, h0, U0

Inner surface

Di,  Ai, hi, Ui

k=0.607 W/m.°Cν=μρ=0.894×10−6 m2/sPr=6.14

Analysis The Reynolds number is

Re=VavgDν=(3 m/s)(0.013 m)0.894×10−6 m2/s=43,624

which is greater than 10,000. Therefore, we assume fully developed turbulent flow, and determine Nusselt number from

Nu=0.023Re0.8Pr0.40.023(43,624)0.8(6.14)0.4=245

and

hi=kDNu=0.607 W/m.°C0.013 m(245)=11,440 W/m2.°C

The inner and the outer surface areas of the tube are

Ai=πDiL=π(0.013 m)(1 m)=0.04084 m2Ao=πDoL=π(0.015 m)(1 m)=0.04712 m2

The total thermal resistance of this heat exchanger per unit length is

R=1hiAi+ln(DoDi)2πkL+1hoAo1(11,440 W/m2.°C)(0.04084 m2)+ln(1.51.3)2π(110 W/m.°C)(1 m)+1(35 W/m2.°C)(0.04712 m2)0.609°C/W

Then the overall heat transfer coefficient of this heat exchanger based on the inner surface becomes

R=1UiAiUi=1RAi=1(0.609°C/W)(0.04084 m2)=40.2 W/m2.°C

16-125 Hot oil is cooled by water in a multi-pass shell-and-tube heat exchanger. The overall heat transfer coefficient based on the inner surface is to be determined.

Assumptions 1 Water flow is fully developed. 2 Properties of the water are constant.

Properties The properties of water at 25C are (Table A-15)

Outer surface

D0, A0, h0, U0

Inner surface

Di,  Ai, hi, Ui

k=0.607 W/m.°Cν=μρ=0.894×10−6 m2/sPr=6.14

Analysis The Reynolds number is

Re=VavgDν=(3 m/s)(0.013 m)0.894×10−6 m2/s=43,624

which is greater than 10,000. Therefore, we assume fully developed turbulent flow, and determine Nusselt number from

Nu=0.023Re0.8Pr0.40.023(43,624)0.8(6.14)0.4=245

and

hi=kDNu=0.607 W/m.°C0.013 m(245)=11,440 W/m2.°C

The inner and the outer surface areas of the tube are

Ai=πDiL=π(0.013 m)(1 m)=0.04084 m2Ao=πDoL=π(0.015 m)(1 m)=0.04712 m2

The total thermal resistance of this heat exchanger per unit length of it with a fouling factor is

R=1hiAi+ln(DoDi)2πkL+Rf,oAo+1hoAo1(11,440 W/m2.°C)(0.04084 m2)+ln(1.51.3)2π(110 W/m.°C)(1 m)+0.0004 m2.°C/W0.04712 m2+1(35 W/m2.°C)(0.04712 m2)0.617°C/W

Then the overall heat transfer coefficient of this heat exchanger based on the inner surface becomes

R=1UiAiUi=1RAi=1(0.617°C/W)(0.04084 m2)=39.7 W/m2.°C

16-126 Water is heated by hot oil in a multi-pass shell-and-tube heat exchanger. The rate of heat transfer and the heat transfer surface area on the outer side of the tube are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the water and oil are given to be 4.18 and 2.2 kJ/kg.C, respectively.

Analysis (a)The rate of heat transfer in this heat exchanger is

Q=mhcph(Th,in−Th,out)=(3 kg/s)(2.2 kJ/kg.°C)(130°C−60°C)=462 kW

(b) The outlet temperature of the cold water is

Q=mccpc(Tc,out−Tc,in)Tc,out=Tc,in+Qmccpc=20°C+462 kW(3 kg/s)(4.18 kJ/kg.°C)=56.8°C

The temperature differences at the two ends are

Hot Oil

130C

3 kg/s

Cold Water

20C

3 kg/s

(20 tube passes)

60C

ΔT1=Th,in−Tc,out=130°C−56.8°C=73.2°CΔT2=Th,out−Tc,in=60°C−20°C=40°C

The logarithmic mean temperature difference is

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=73.2−40ln(73.240)=54.9°C

and

P=t2−t1T1−t1=56.8−20130−20=0.335F=0.96

The heat transfer surface area on the outer side of the tube is then determined from

Q=UAsFΔTlmAs=QUFΔTlm=462 kW(0.22 kW/m2.°C)(0.96)(54.9°C)=39.8 m2

16-127E Water is heated by solar-heated hot air in a double-pipe counter-flow heat exchanger. The required length of the tube is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the water and air are given to be 1.0 and 0.24 Btu/lbm.F, respectively.

Analysis The rate of heat transfer in this heat exchanger is

Q=mhcph(Th,in−Th,out)=(0.7 lbm/s)(0.24 Btu/lbm.°F)(190°F−135°F)=9.24 Btu/s

The outlet temperature of the cold water is

Q=mccpc(Tc,out−Tc,in)Tc,out=Tc,in+Qmccpc=70°F+9.24 Btu/s(0.35 lbm/s)(1.0 Btu/lbm.°F)=96.4°F

Hot Air

190F

0.7 lbm/s

Cold Water

70F

0.35 lbm/s

135F

The temperature differences at the two ends are

ΔT1=Th,in−Tc,out=190°F−96.4°F=93.6°FΔT2=Th,out−Tc,in=135°F−70°F=65°F

The logarithmic mean temperature difference is

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=93.6−65ln(93.665)=78.43°F

The heat transfer surface area on the outer side of the tube is determined from

Q=UAsΔTlmAs=QUΔTlm=9.24 Btu/s(203600 Btu/s.ft2.°F)(78.43°F)=21.21 ft2

Then the length of the tube required becomes

As=πDLL=AsπD=21.21 ft2π(0.512 ft)=162.0 ft

16-128 It is to be shown that when T1 = T2 for a heat exchanger, the Tlm relation reduces to Tlm = T1 = T2.

Analysis When T1 = T2, we obtain

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=00

This case can be handled by applying L'Hospital's rule (taking derivatives of nominator and denominator separately with respect to ). That is,

ΔTlm=d(ΔT1−ΔT2)dΔT1d[ln(ΔT1ΔT2)]dΔT1=11ΔT1=ΔT1=ΔT2

16-129 Refrigerant-134a is condensed by air in the condenser of a room air conditioner. The heat transfer area on the refrigerant side is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and  potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Air

25C

R-134a

40C

40C

35C

Properties The specific heat of air is given to be 1.005 kJ/kg.C.

Analysis The temperature differences at the two ends are

ΔT1=Th,in−Tc,out=40°C−35°C=5°CΔT2=Th,out−Tc,in=40°C−25°C=15°C

The logarithmic mean temperature difference is

ΔTlm=ΔT1−ΔT2ln(ΔT1ΔT2)=5−15ln(515)=9.1°C

The heat transfer surface area on the outer side of the tube is determined from

Q=UAsΔTlmAs=QUΔTlm=(15,0003600) kW(0.150 kW/m2.°C)(9.1°C)=3.05 m2

16-130 Air is preheated by hot exhaust gases in a cross-flow heat exchanger. The rate of heat transfer is to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of air and combustion gases are given to be 1.005 and 1.1 kJ/kg.C, respectively.

Analysis The rate of heat transfer is simply

Q=[mcp(Tin−Tout)]gas.=(0.65 kg/s)(1.1 kJ/kg.°C)(180°C−95°C)=60.8 kW

16-131 A water-to-water heat exchanger is proposed to preheat the incoming cold water by the drained hot water in a plant to save energy. The heat transfer rating of the heat exchanger and the amount of money this heat exchanger will save are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible.

Properties The specific heat of the hot water is given to be 4.18 kJ/kg.C.

Hot water

60C

8 kg/s

Cold Water

14C

Analysis The maximum rate of heat transfer is

Qmax=mhcph(Th,in−Tc,in)(860 kg/s)(4.18 kJ/kg.°C)(60°C−14°C)25.6 kW

Noting that the heat exchanger will recover 72% of it, the actual heat transfer rate becomes

Q=εQmax=(0.72)(25.6 kJ/s)=18.43 kW

which is the heat transfer rating. The operating hours per year are

The annual operating hours = (8 h/day)(5 days/week)(52 week/year) = 2080 h/year

The energy saved during the entire year will be

Energy saved = (heat transfer rate)(operating time)

= (18.43 kJ/s)(2080 h/year)(3600 s/h)

= 1.38x108  kJ/year

Then amount of fuel and money saved will be

Fuel saved=Energy savedFurnace efficiency=1.38×108 kJ/year0.781 therm105,500 kJ                                                    =1677 therms/year

Money saved = (fuel saved)(the price of fuel)

=  (1677 therms/year)($1.00/therm) = $1677/year

16-132 A shell-and-tube heat exchanger is used to heat water with geothermal steam condensing. The rate of heat transfer, the rate of condensation of steam, and the overall heat transfer coefficient are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant.

Properties The heat of vaporization of geothermal water at 120C is given to be hfg = 2203 kJ/kg and specific heat of water is given to be cp = 4180 J/kg.C.

Steam

120C

22C

Water

3.9 kg/s

14 tubes

120C

Analysis (a) The outlet temperature of the water is

Tc,out=Th,out−46=120°C−46°C=74°C

Then the rate of heat transfer becomes

Q=[mcp(Tout−Tin)]water(3.9 kg/s)(4.18 kJ/kg.°C)(74°C−22°C)847.7 kW

(b) The rate of condensation of steam is determined from

Q=(mhfg)geothermalsteam847.7 kW=m(2203 kJ/kg)m=0.385 kg/s

(c) The heat transfer area is

Ai=nπDiL=14π(0.024 m)(3.2 m)=3.378 m2

The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=120°C−74°C=46°CΔT2=Th,out−Tc,in=120°C−22°C=98°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=46−98ln(4698)=68.8°C

P=t2−t1T1−t1=74−22120−22=0.53F=1

Then the overall heat transfer coefficient is determined to be

Q=UiAiFΔTlm,CFUi=QAiFΔTlm,CF=847,700 W(3.378 m2)(1)(68.8°C)=3650 W/m2.°C

16-133 Water is heated by geothermal water in a double-pipe counter-flow heat exchanger. The mass flow rate of the geothermal water and the outlet temperatures of both fluids are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the geothermal water and the cold water are given to be 4.25 and 4.18 kJ/kg.°C, respectively.

Analysis The heat capacity rates of the hot and cold fluids are

Geothermal water

75°C

Cold Water

17°C

1.2 kg/s

Ch=mhcph=mh(4.25 kJ/kg.°C)=4.25 {mhCc=mccpc=(1.2 kg/s)(4.18 kJ/kg.°C)=5.016 kW/°C

Cmin=Cc=5.016 kW/°C

and	c=CminCmax=5.0164.25 {mh=1.1802mh

The NTU of this heat exchanger is

NTU=UAsCmin=(0.480 kW/m2.°C)(25 m2)5.016 kW/°C=2.392

Using the effectiveness relation, we find the capacity ratio

ε=1−exp−NTU(1−c)1−cexp−NTU(1−c)0.823=1−exp−2.392(1−c)1−cexp−2.392(1−c)c=0.494

Then the mass flow rate of geothermal water is determined from

c=1.1802mh0.494=1.1802mhmh=2.39 kg/s

The maximum heat transfer rate is

Qmax=Cmin(Th,in−Tc,in)=(5.016 kW/°C)(75°C-17°C)=290.9 kW

Then the actual rate of heat transfer rate becomes

Q=εQmax=(0.823)(290.9 kW)=239.4 kW

The outlet temperatures of the geothermal and cold waters are determined to be

Q=Cc(Tc,out−Tc,in)239.4 kW=(5.016 kW/°C)(Tc,out−17)Tc,out=64.7°C

Q=mhcph(Th,in−Th,out)239.4 kW=(2.39 kg/s)(4.25 kJ/kg.°C)(75−Th,out)Th,out=51.4°C

16-134 Air is to be heated by hot oil in a cross-flow heat exchanger with both fluids unmixed. The effectiveness of the heat exchanger, the mass flow rate of the cold fluid, and the rate of heat transfer are to be determined.

.Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of the air and the oil are given to be 1.006 and 2.15 kJ/kg.°C, respectively.

Analysis (a) The heat capacity rates of the hot and cold fluids are

Air

18°C

Oil

80°C

58°C

Ch=mhcph=0.5mc(2.15 kJ/kg.°C)=1.075 {mcCc=mccpc=mc(1.006 kJ/kg.°C)=1.006 {mc

Therefore,   Cmin=Cc=1.006 {mc

and	c=CminCmax=1.006 {mc1.075 {mc=0.936

The effectiveness of the heat exchanger is determined from

ε=QQmax=Cc(Tc,out−Tc,in)Cc(Th,in−Tc,in)=58−1880−18=0.645

(b) The NTU of this heat exchanger is expressed as

NTU=UAsCmin=(0.750 kW/°C)1.006 {mc=0.7455mc

The NTU of this heat exchanger can also be determined from

NTU=−lncln(1−ε)+1c=−ln0.936×ln(1−0.645)+10.936=3.724

Then the mass flow rate of the air is determined to be

NTU=UAsCmin3.724=(0.750 kW/°C)1.006 {mcmc=0.20 kg/s

(c) The rate of heat transfer is determined from

Q=mccpc(Tc,out−Tc,in)=(0.20 kg/s)(1.006 kJ/kg.°C)(58-18)°C=8.05 kW

16-135 A water-to-water counter-flow heat exchanger is considered. The outlet temperature of the cold water, the effectiveness of the heat exchanger, the mass flow rate of the cold water, and the heat transfer rate are to be determined.

.Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 The overall heat transfer coefficient is constant and uniform.

Properties The specific heats of both the cold and the hot water are given to be 4.18 kJ/kg.°C.

Analysis (a) The heat capacity rates of the hot and cold fluids are

Hot water

95°C

Cold Water

20°C

Ch=mhcph=1.5mc(4.18 kJ/kg.°C)=6.27 {mcCc=mccpc=mc(4.18 kJ/kg.°C)=4.18 {mc

Therefore,   Cmin=Cc=4.18 {mc

and	C=CminCmax=4.18 {mc6.27 {mc=0.667

The rate of heat transfer can be expressed as

Q=Cc(Tc,out−Tc,in)=(4.18 {mc)(Tc,out−20)				Q=Ch(Th,in−Th,out)=(6.27 {mc)95−(Tc,out+15)=(6.27 {mc)(80−Tc,out)

Setting the above two equations equal to each other we obtain the outlet temperature of the cold water

Q=4.18 {mc(Tc,out−20)=6.27 {mc(80−Tc,out)Tc,out=56°C

(b) The effectiveness of the heat exchanger is determined from

ε=QQmax=Cc(Tc,out−Tc,in)Cc(Th,in−Tc,in)=4.18 {mc(56−20)4.18 {mc(95−20)=0.48

(c) The NTU of this heat exchanger is determined from

NTU=1c−1lnε−1εc−1=10.667−1ln0.48−10.48×0.667−1=0.805

Then, from the definition of NTU, we obtain the mass flow rate of the cold fluid:

NTU=UAsCmin0.805=1.400 kW/°C4.18 {mcmc=0.416 kg/s

(d) The rate of heat transfer is determined from

Q=mccpc(Tc,out−Tc,in)=(0.416 kg/s)(4.18 kJ/kg.°C)(56−20)°C=62.6 kW

16-136 Oil is cooled by water in a 2-shell passes and 4-tube passes heat exchanger. The mass flow rate of water and the surface area are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant. 5 There is no fouling.

Properties The specific heat of oil is given to be 2 kJ/kg.C. The specific heat of water is taken to be 4.18 kJ/kg.C.

Water

25C

Oil

125C

55C

2 shell passes

4 tube passes

46C

Analysis The logarithmic mean temperature difference for counter-flow arrangement and the correction factor F are

ΔT1=Th,in−Tc,out=125°C−46°C=79°CΔT2=Th,out−Tc,in=55°C−25°C=30°C

ΔTlm,CF=ΔT1−ΔT2ln(ΔT1ΔT2)=79−30ln(7930)=50.61°C

P=t2−t1T1−t1=55−12525−125=0.7F=0.97 (Fig. 16-18)

The rate of heat transfer is

Q=mhch(Th,in−Th,out)=(10 kg/s)(2.0 kJ/kg⋅°C)(125−55)°C=1400 kW

The mass flow rate of water is

mw=Qcp(Tout−Tin)=1400 kW(4.18 kJ/kg.°C)(46°C−25°C)=15.9 kg/s

The surface area of the heat exchanger is determined to be

Q=UAFΔTlm1400 kW=(0.9 kW/m2⋅C)As(0.97)(50.61°C)As=31.7 m2

- 16-137 A polymer solution is heated by ethylene glycol in a parallel-flow heat exchanger. The rate of heat transfer, the outlet temperature of polymer solution, and the mass flow rate of ethylene glycol are to be determined.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant. 5 There is no fouling.

Properties The specific heats of polymer and ethylene glycol are given to be 2.0 and 2.5 kJ/kg.C, respectively.

ethylene

60C

Polymer

20C

0.3 kg/s

Analysis (a) The logarithmic mean temperature difference is

ΔT1=Th,in−Tc,in=60°C−20°C=40°CΔT2=Th,out−Tc,out=15°C

ΔTlm,PF=ΔT1−ΔT2ln(ΔT1ΔT2)=40−15ln(4015)=25.49°CThe rate of heat transfer in this heat exchanger is

Q=UAsΔTlm=(240 W/m2.°C)(0.8 m2)(25.49°C)=4894 W

(b) The outlet temperatures of both fluids are

Q=mccc(Tc,out−Tc,in)→Tc,out=Tc,in+Qmccc=20°C+4894 W(0.3 kg/s)(2000 J/kg⋅°C)=28.2°CTh,out=ΔTout+Tc,out=15°C+28.2°C=43.2°C

(c) The mass flow rate of ethylene glycol is determined from

methylene=Qcp(Tout−Tin)=4894 W(2500 kJ/kg.°C)(60°C−43.2°C)=0.117 kg/s

16-138 The inlet and exit temperatures and the volume flow rates of hot and cold fluids in a heat exchanger are given. The rate of heat transfer to the cold water, the overall heat transfer coefficient, the fraction of heat loss, the heat transfer efficiency, the effectiveness, and the NTU of the heat exchanger are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Changes in the kinetic and potential energies of fluid streams are negligible. 3 Fluid properties are constant.

Properties The densities of hot water and cold water at the average temperatures of (38.9+27.0)/2 = 33.0C and (14.3+19.8)/2 = 17.1C are 994.8 and 998.6 kg/m3, respectively. The specific heat at the average temperature is 4178 J/kg.C for hot water and 4184 J/kg.C for cold water (Table A-15).

Analysis (a) The mass flow rates are

mh=ρhVh=(994.8 kg/m3)(0.0025/60 m3/s)=0.04145 kg/s

mc=ρcVc=(998.6 kg/m3)(0.0045/60 m3/s)=0.07490 kg/s

The rates of heat transfer from the hot water and to the cold water are

Qh=[mcp(Tin−Tout)]h=(0.04145 kg/s)(4178 kJ/kg.°C)(38.9°C−27.0°C)=2061 W

Qc=[mcp(Tout−Tin)]c=(0.07490 kg/s)(4184 kJ/kg.°C)(19.8°C−14.3°C)=1724 W

(b) The logarithmic mean temperature difference and the overall heat transfer coefficient are

ΔT1=Th,in−Tc,out=38.9°C−19.8°C=19.1°C

Hot

water

38.9C

Cold water

14.3C

19.8C

27.0C

ΔT2=Th,out−Tc,in=27.0°C−14.3°C=12.7°C

ΔTlm=ΔT1−ΔT2lnΔT1ΔT2=19.1−12.7ln19.112.7=15.68°C

U=Qhc,mAΔTlm=(1724+2061)2 W(0.04 m2)(15.68°C)=3017 W/m2⋅C

Note that we used the average of two heat transfer rates in calculations.

(c) The fraction of heat loss and the heat transfer efficiency are

floss=Qh−QcQh=2061−17242061=0.164=16.4%η=QcQh=17242061=0.836=83.6%(d) The heat capacity rates of the hot and cold fluids are

Ch=mhcph=(0.04145 kg/s)(4178 kJ/kg.°C)=173.2 W/°CCc=mccpc=(0.07490 kg/s)(4184 kJ/kg.°C)=313.4 W/°C

Therefore

Cmin=Ch=173.2 W/°C

which is the smaller of the two heat capacity rates. Then the maximum heat transfer rate becomes

Qmax=Cmin(Th,in−Tc,in)=(173.2 W/°C)(38.9°C-14.3°C)=4261 W

The effectiveness of the heat exchanger is

ε=QQmax=(1724+2061)2 kW4261 kW=0.444=44.4%

One again we used the average heat transfer rate. We could have used the smaller or greater heat transfer rates in calculations. The NTU of the heat exchanger is determined from

NTU=UACmin=(3017 W/m2⋅C)(0.04 m2)173.2 W/°C=0.697

16-139 . . .  16-143 Design and Essay Problems

16-143 A counter flow double-pipe heat exchanger is used for cooling a liquid stream by a coolant. The rate of heat transfer and the outlet temperatures of both fluids are to be determined. Also, a replacement proposal is to be analyzed.

Assumptions 1 Steady operating conditions exist. 2 The heat exchanger is well-insulated so that heat loss to the surroundings is negligible and thus heat transfer from the hot fluid is equal to the heat transfer to the cold fluid. 3 Changes in the kinetic and potential energies of fluid streams are negligible. 4 Fluid properties are constant. 5 There is no fouling.

Properties The specific heats of hot and cold fluids are given to be 3.15 and 4.2 kJ/kg.C, respectively.

Analysis (a) The overall heat transfer coefficient is

Cold

10C

8 kg/s

Hot

90C

10 kg/s

U=6001mc0.8+2mh0.8=600180.8+2100.8=1185 W/m2.K

The rate of heat transfer may be expressed as

Q=mccc(Tc,out−Tc,in)=(8)(4200)(Tc,out−10) 	(1)

Q=mhch(Th,in−Th,out)=(10)(3150)(90−Th,out) 	(2)

It may also be expressed using the logarithmic mean temperature difference as

Q=UAΔTlm=UAΔT1−ΔT2ln(ΔT1ΔT2)=(1185)(9)(90−Tc)−(Th−10)ln90−TcTh−10   	(3)

We have three equations with three unknowns, solving an equation solver such as EES, we obtain

Q=6.42×105 W,   Tc,out=29.1°C,   Th,out=69.6°C

(b) The overall heat transfer coefficient for each unit is

U=6001mc0.8+2mh0.8=600140.8+250.8=680.5 W/m2.K

Then

Q=mccc(Tc,out−Tc,in)=(2×4)(4200)(Tc,out−10)			 (1)

Q=mhch(Th,in−Th,out)=(2×5)(3150)(90−Th,out) 			 (2)

Q=UAΔTlm=UAΔT1−ΔT2ln(ΔT1ΔT2)=(680.5)(2×5)(90−Tc)−(Th−10)ln90−TcTh−10  	 (3)

Once again, we have three equations with three unknowns, solving an equation solver such as EES, we obtain

Q=4.5×105 W,   Tc,out=23.4°C,   Th,out=75.7°C

Discussion Despite a higher heat transfer area, the new heat transfer is about 30% lower. This is due to much lower U, because of the halved flow rates. So, the vendor’s recommendation is not acceptable. The vendor’s unit will do the job provided that they are connected in series. Then the two units will have the same U as in the existing unit.

